## Cover
Advanced Energy Audit
Audit workbook: every figure as a live formula, tagged by how it was obtained
Demo Foods (Pty) Ltd (fictional)
FICTIONAL DEMONSTRATION: this site, its bills, readings, quotes and rates are invented. It is not a real company, site or client.
The audit
Site | Demo Foods (Pty) Ltd (fictional)
Sector | Food processing: bakery and cold storage
Location | Gauteng, South Africa (fictional site)
Audit period | July 2025 to June 2026
Prepared for | Demo Foods (Pty) Ltd (fictional)
Prepared by | Thabiso Kali, Certified Energy Manager
Audit standard | ISO 50002-1:2025 detailed audit; ASHRAE Standard 211 Level 2, refrigeration at Level 3
Report date | 2026-10-19
Workbook made | 2026-10-21
Project file | p-demo-foods · last saved 2026-10-19
Basis | Nominal rand; annual, end-of-year cash flows; year 0 = now. Energy in kWh (fuels converted at the edge).
Headline results (links to the Portfolio and Balance sheets)
Measures | 24
Capex | 3497273.8328
Net saving, year 1 (R/yr) | 3266550.9928
Energy saved (kWh/yr) | 1873002.885
Simple payback (years) | 1.0706
NPV at 12.0% | 23587953.9595
IRR | 99.77%
Cost of saved energy (R/kWh) | 0.30506
Balance points within tolerance | 3 of 3
Site energy unaccounted (share of metered) | 4.642%
Data levels: how good the data behind each system is
System | Data level | How its energy is estimated
Compressed air | Level 2: equipment inventory | equipment register, bottom-up E = n × P × LF × h / η (about ±20%)
Refrigeration and chillers | Level 3: interval data | interval or sub-meter data, annualised; regression baselines (about ±10-15%)
Steam and boilers | Level 2: equipment inventory | equipment register, bottom-up E = n × P × LF × h / η (about ±20%)
Motors, pumps and fans | Level 2: equipment inventory | equipment register, bottom-up E = n × P × LF × h / η (about ±20%)
Process heat | Level 2: equipment inventory | equipment register, bottom-up E = n × P × LF × h / η (about ±20%)
Lighting | Level 2: equipment inventory | equipment register, bottom-up E = n × P × LF × h / η (about ±20%)
HVAC and offices | Level 2: equipment inventory | equipment register, bottom-up E = n × P × LF × h / η (about ±20%)
Electrical supply and tariff | Level 1: bills | the carrier's metered total × a share from the walk-through (about ±30%)
Target data level agreed in the scope: Level 2: equipment inventory.
How to read this workbook
1 234 | Input: a number you may change. Every sheet that uses it follows.
=formula | Formula: worked out from the cells it names.
=Sheet!A1 | Link: a number brought from another sheet.
value | Worked out by the studio's models (a system model, the ±, a recorded factor); its source is beside it.
R 1 234 | Headline result.
measured | Read from a meter, bill, nameplate or log.
calculated | Worked out by a tool from the inputs entered.
estimated | A figure you entered: a quote, a judgement or your own rate.
assumed | A default the tools supplied. Replace it with your own figure.
A result is only as good as its weakest input: each measure's tag is the weakest of its numbers that matter.
Sheets
Inputs | Discount rate, escalation, the analysis period, the tariff rates from the bills and the balance tolerances, each a named range.
Bills | Every bill as entered, and what the latest 12 add up to per account: metered kWh and the average rates.
Inventory | The equipment register with the live formula E = n × P × Σ(LF × h) / η per item.
Balance | Metered against bottom-up at each balance point: gap, tolerance, status and the unaccounted remainder; flows, conversions, terms and nodes.
Measures | Each measure's inputs: kWh saved by carrier, rand saved by tariff component, capex, running cost, life, timing and tags.
CashFlows | Year-by-year cash flow of every measure and of the portfolio, with escalation and discount factors.
Portfolio | Simple payback, NPV, IRR and the levelised cost of saved energy per measure and in total, and the cost curve (MACC).
Loan | If a term loan pays for the measures: the loan the savings carry at a target DSCR, the annuity schedule, the DSCR by year and the equity cash flow.
Sources & methods | The method notes behind each sheet, the sources they cite and the workbook's conventions.
Disclaimer
Savings are engineering estimates from the data listed in this workbook. Figures tagged estimated or assumed should be confirmed before an investment decision; budget costs are not quotes, and no measure is guaranteed until it is measured and verified.
The financial figures are a business case, not investment, tax or legal advice. Tariffs, escalation and the discount rate are the stated assumptions on the Inputs sheet.
This is a fictional demonstration: Demo Foods (Pty) Ltd and every name and number in it are invented, and nothing comes from any real company, client or employer.

## Inputs
Inputs
The settings and rates every other sheet calculates from. Amber cells are inputs: change one and the workbook follows.
FICTIONAL DEMONSTRATION: Demo Foods (Pty) Ltd (fictional). Every name and number is invented.
Valuation settings (studio step 8)
Input | Value | Unit | Tag | ± (%) | Named range | Source and notes
Discount rate | 12% | per year | assumed |  | DiscountRate | Nominal, the client's hurdle rate. A valuation choice, not data (assumed while it is the studio's default).
Tariff escalation | 8% | per year | assumed |  | Escalation | Applied to savings and running costs from year 2: year 1 is at today's tariff, (1 + e)^(t − 1) after that.
Analysis period | 20 | years | calculated |  | AnalysisPeriod | The longest measure life in whole years: the length of the portfolio cash flow. Each measure's savings stop at the end of its own life; none is replaced.
Year columns on CashFlows | 20 | years | calculated |  | CashFlowYears | CashFlows runs from year 0 to this year (the longest life when the workbook was made).
Check: the year columns cover the analysis period | OK
Tariff rates from the bills (average of the latest 12 bills, lib/audit/bills.ts)
Input | Value | Unit | Tag | ± (%) | Named range | Source and notes
Energy rate, electricity | 1.4966 | R/kWh | calculated | 2 | EnergyRate_Electricity | Eskom account (fictional number): energy charges ÷ kWh over 12 bills (average across time-of-use periods)
Demand rate, electricity | 42 | R/kVA/month | calculated | 2 | DemandRate_Electricity | Eskom account (fictional number): demand charges ÷ billed kVA over 12 bills
Capacity rate, electricity | 24 | R/kVA/month | calculated | 2 | CapacityRate_Electricity | Eskom account (fictional number): capacity charges ÷ (NMD 650 kVA × 12 months)
Energy rate, lpg | 1.8647 | R/kWh | assumed | 2 | EnergyRate_LPG | Bulk LPG supply (fictional supplier): cost ÷ kWh (kg × 13.139 kWh/kg) over 12 bills
Energy rate, diesel | 2.2724 | R/kWh | assumed | 2 | EnergyRate_Diesel | Diesel for the standby generator (fictional supplier): cost ÷ kWh (litre × 10.033 kWh/litre) over 12 bills
An average energy rate suits a saving spread like the site's load; a saving in peak or off-peak hours is worth more or less (Sources & methods, section 9).
Energy balance settings (studio step 3)
Input | Value | Unit | Tag | ± (%) | Named range | Source and notes
Balance tolerance | 10% | ± of metered | assumed |  | BalanceTolerance | A balance point closes when ¦metered − bottom-up¦ ≤ this share of metered (LEED existing-buildings benchmark; Sources & methods, section 5).
Tolerance where every node is at data level 4 | 5% | ± of metered | assumed |  | BalanceToleranceL4 | Process measurements behind every node (Australian EEO assessment framework benchmark; Sources & methods, section 5).
Scale estimated items to close the balance | No |  |  |  |  | Off: the balance is never forced; the remainder is shown as unaccounted.
Not used in this audit
Grid emission factor and carbon tax: the audit project carries none, so the workbook has no carbon figures and the valuation has no carbon tax.

## Bills
Bills
Each carrier account's monthly bills (the latest 12 count) and what they add up to: the metered totals and the average rates.
FICTIONAL DEMONSTRATION: Demo Foods (Pty) Ltd (fictional). Every name and number is invented.
Carrier accounts: annual totals and average rates from the latest 12 bills (one column per account)
Figure | Unit | acc-grid | acc-lpg | acc-diesel
Name |  | Eskom account (fictional number) | Bulk LPG supply (fictional supplier) | Diesel for the standby generator (fictional supplier)
Carrier |  | electricity | lpg | diesel
Balance node |  | grid | lpg | diesel
Billing unit |  | kWh | kg | litre
kWh per billing unit | kWh/unit | 1 | 13.1389 | 10.0333
Heating-value basis |  | — | LHV | LHV
Conversion tag |  | measured | assumed | assumed
Bills counted (latest 12) | bills | 12 | 12 | 12
Quantity billed | billing unit | 2945004 | 297001 | 6500
Annualisation (12 ÷ bills when fewer than 12) | × | 1 | 1 | 1
Metered energy | kWh/yr | 2945004 | 3902263.1389 | 65216.6667
Metered tag |  | measured | assumed | assumed
Meter and conversion ± | % | 2 | 4.2426 | 5.831
Energy charges | R | 4407542.52 | 7276524.5 | 148200
kWh billed (quantity × kWh per unit) | kWh | 2945004 | 3902263.1389 | 65216.6667
Energy rate (energy charges ÷ kWh billed) | R/kWh | 1.4966 | 1.8647 | 2.2724
Demand charges (bills with a billed kVA) | R | 273882 | 0 | 0
Billed kVA, summed over those bills | kVA | 6521 | 0 | 0
Demand rate (demand charges ÷ billed kVA) | R/kVA/month | 42 | 0 | 0
Capacity charges | R | 187200 | 0 | 0
Notified maximum demand (NMD) | kVA | 650
Capacity rate (capacity charges ÷ (NMD × bills)) | R/kVA/month | 24 | 0 | 0
Total cost | R | 4907024.52 | 7276524.5 | 148200
Monthly bills (as entered in step 2; the latest 12 per account count)
Account | Month | Quantity (billing unit) | Unit | Reading tag | Energy charges (R) (total cost where the bill has no split) | Demand charges (R) | Capacity charges (R) | Fixed charges (R) | Total cost (R) | Maximum demand (kVA) | kW at maximum demand | Power factor at maximum demand | In the latest 12 (1/0) | Counts for the demand rate (1/0) | Note
acc-grid | 2025-07 | 237392 | kWh | measured | 521788.64 | 21630 | 15600 | 3200 | 562218.64 | 515 | 443 | 0.86019 | 1 | 1
acc-grid | 2025-08 | 227192 | kWh | measured | 499369.04 | 20706 | 15600 | 3200 | 538875.04 | 493 | 424 | 0.86004 | 1 | 1
acc-grid | 2025-09 | 239492 | kWh | measured | 306358.24 | 22302 | 15600 | 3200 | 347460.24 | 531 | 462 | 0.87006 | 1 | 1
acc-grid | 2025-10 | 246692 | kWh | measured | 315568.48 | 22512 | 15600 | 3200 | 356880.48 | 536 | 461 | 0.86007 | 1 | 1
acc-grid | 2025-11 | 263792 | kWh | measured | 337442.8 | 25158 | 15600 | 3200 | 381400.8 | 599 | 509 | 0.84975 | 1 | 1
acc-grid | 2025-12 | 268892 | kWh | measured | 343966.72 | 24528 | 15600 | 3200 | 387294.72 | 584 | 502 | 0.85959 | 1 | 1
acc-grid | 2026-01 | 248792 | kWh | measured | 318254.8 | 22386 | 15600 | 3200 | 359440.8 | 533 | 464 | 0.87054 | 1 | 1
acc-grid | 2026-02 | 260192 | kWh | measured | 332837.68 | 26292 | 15600 | 3200 | 377929.68 | 626 | 538 | 0.85942 | 1 | 1
acc-grid | 2026-03 | 248192 | kWh | measured | 317487.28 | 22890 | 15600 | 3200 | 359177.28 | 545 | 463 | 0.84954 | 1 | 1
acc-grid | 2026-04 | 240392 | kWh | measured | 307509.52 | 22680 | 15600 | 3200 | 348989.52 | 540 | 464 | 0.85926 | 1 | 1
acc-grid | 2026-05 | 231692 | kWh | measured | 296380.48 | 20916 | 15600 | 3200 | 336096.48 | 498 | 433 | 0.86948 | 1 | 1
acc-grid | 2026-06 | 232292 | kWh | measured | 510578.84 | 21882 | 15600 | 3200 | 551260.84 | 521 | 448 | 0.85988 | 1 | 1
acc-lpg | 2025-07 | 24027 | kg | measured | 588661.5 |  |  |  | 588661.5 |  |  |  | 1 | 0 | Supplier tank telemetry, month-end readings (fictional)
acc-lpg | 2025-08 | 25397 | kg | measured | 622226.5 |  |  |  | 622226.5 |  |  |  | 1 | 0 | Supplier tank telemetry, month-end readings (fictional)
acc-lpg | 2025-09 | 24560 | kg | measured | 601720 |  |  |  | 601720 |  |  |  | 1 | 0 | Supplier tank telemetry, month-end readings (fictional)
acc-lpg | 2025-10 | 24636 | kg | measured | 603582 |  |  |  | 603582 |  |  |  | 1 | 0 | Supplier tank telemetry, month-end readings (fictional)
acc-lpg | 2025-11 | 26462 | kg | measured | 648319 |  |  |  | 648319 |  |  |  | 1 | 0 | Supplier tank telemetry, month-end readings (fictional)
acc-lpg | 2025-12 | 26767 | kg | measured | 655791.5 |  |  |  | 655791.5 |  |  |  | 1 | 0 | Supplier tank telemetry, month-end readings (fictional)
acc-lpg | 2026-01 | 22505 | kg | measured | 551372.5 |  |  |  | 551372.5 |  |  |  | 1 | 0 | Supplier tank telemetry, month-end readings (fictional)
acc-lpg | 2026-02 | 24179 | kg | measured | 592385.5 |  |  |  | 592385.5 |  |  |  | 1 | 0 | Supplier tank telemetry, month-end readings (fictional)
acc-lpg | 2026-03 | 24484 | kg | measured | 599858 |  |  |  | 599858 |  |  |  | 1 | 0 | Supplier tank telemetry, month-end readings (fictional)
acc-lpg | 2026-04 | 24940 | kg | measured | 611030 |  |  |  | 611030 |  |  |  | 1 | 0 | Supplier tank telemetry, month-end readings (fictional)
acc-lpg | 2026-05 | 24408 | kg | measured | 597996 |  |  |  | 597996 |  |  |  | 1 | 0 | Supplier tank telemetry, month-end readings (fictional)
acc-lpg | 2026-06 | 24636 | kg | measured | 603582 |  |  |  | 603582 |  |  |  | 1 | 0 | Supplier tank telemetry, month-end readings (fictional)
acc-diesel | 2025-07 | 0 | litre | measured | 0 |  |  |  | 0 |  |  |  | 1 | 0
acc-diesel | 2025-08 | 3000 | litre | measured | 68400 |  |  |  | 68400 |  |  |  | 1 | 0 | Delivery note (fictional)
acc-diesel | 2025-09 | 0 | litre | measured | 0 |  |  |  | 0 |  |  |  | 1 | 0
acc-diesel | 2025-10 | 0 | litre | measured | 0 |  |  |  | 0 |  |  |  | 1 | 0
acc-diesel | 2025-11 | 0 | litre | measured | 0 |  |  |  | 0 |  |  |  | 1 | 0
acc-diesel | 2025-12 | 0 | litre | measured | 0 |  |  |  | 0 |  |  |  | 1 | 0
acc-diesel | 2026-01 | 2000 | litre | measured | 45600 |  |  |  | 45600 |  |  |  | 1 | 0 | Delivery note (fictional)
acc-diesel | 2026-02 | 0 | litre | measured | 0 |  |  |  | 0 |  |  |  | 1 | 0
acc-diesel | 2026-03 | 0 | litre | measured | 0 |  |  |  | 0 |  |  |  | 1 | 0
acc-diesel | 2026-04 | 0 | litre | measured | 0 |  |  |  | 0 |  |  |  | 1 | 0
acc-diesel | 2026-05 | 1500 | litre | measured | 34200 |  |  |  | 34200 |  |  |  | 1 | 0 | Delivery note (fictional)
acc-diesel | 2026-06 | 0 | litre | measured | 0 |  |  |  | 0 |  |  |  | 1 | 0

## Inventory
Inventory
The equipment register. Bottom-up energy per item: E = n × P × Σ(LF × h) / η, with η = 1 for an input rating (Sources & methods, section 4).
FICTIONAL DEMONSTRATION: Demo Foods (Pty) Ltd (fictional). Every name and number is invented.
Item | Description | System | Balance node | Carrier | Count n | Rated power P (kW) | Rating | Efficiency η | Mode 1 | Load factor LF1 | Hours h1 (h/yr) | Mode 2 | Load factor LF2 | Hours h2 (h/yr) | Σ LF × h (h/yr) | Energy E (kWh/yr) | Tag | ± (%) | Used in the balance as | Input tags (M measured, C calculated, E estimated, A assumed) | Notes
ca-comp | Screw compressors, 55 kW fixed speed (fictional make) | Compressed air | ca | electricity | 2 | 61 | input | 1 | Running | 0.6 | 8760 |  |  |  | 5256 | 641232 | estimated | 15.5885 | System model (Balance, terms) | n M · P M · Running: LF E, h M
rf-freezer | Freezer plant compressors (−25 °C store and blast freezer) | Refrigeration and chillers | refrig | electricity | 3 | 37 | input | 1 | Running | 0.55 | 8760 |  |  |  | 4818 | 534798 | estimated | 21.4243 | Cross-check: the node is measured | n M · P M · Running: LF E, h E
rf-chill | Chill plant compressors (+2 °C store and dispatch) | Refrigeration and chillers | refrig | electricity | 2 | 22 | input | 1 | Running | 0.5 | 8760 |  |  |  | 4380 | 192720 | estimated | 21.4243 | Cross-check: the node is measured | n M · P M · Running: LF E, h E
rf-fans | Evaporator fans | Refrigeration and chillers | refrig | electricity | 24 | 0.75 | input | 1 | Running | 0.85 | 8760 |  |  |  | 7446 | 134028 | estimated | 21.4243 | Cross-check: the node is measured | n M · P M · Running: LF E, h E
rf-defrost | Electric defrost heaters | Refrigeration and chillers | refrig | electricity | 18 | 4.5 | input | 1 | Defrosting | 1 | 548 |  |  |  | 548 | 44388 | estimated | 15.5885 | Cross-check: the node is measured | n M · P M · Defrosting: LF M, h E
mo-mixers | Dough mixers | Motors, pumps and fans | motors | electricity | 4 | 30 | output (shaft) | 0.936 | Mixing | 0.45 | 3000 |  |  |  | 1350 | 173076.9231 | estimated | 21.5174 | Inventory (E above) | n M · P M · η M · Mixing: LF E, h E
mo-fans | Oven-hall extraction fans | Motors, pumps and fans | motors | electricity | 2 | 22 | output (shaft) | 0.93 | Running | 0.7684 | 5500 |  |  |  | 4226.2 | 199949.2473 | estimated | 21.5174 | Inventory (E above) | n M · P M · η M · Running: LF E, h E
mo-pumps | Cooling-water and process pumps | Motors, pumps and fans | motors | electricity | 3 | 11 | output (shaft) | 0.914 | Running | 0.7 | 6000 |  |  |  | 4200 | 151641.1379 | estimated | 21.5174 | Inventory (E above) | n M · P M · η M · Running: LF E, h E
mo-conveyors | Conveyors, dividers and moulders | Motors, pumps and fans | motors | electricity | 30 | 1.5 | output (shaft) | 0.828 | Running | 0.55 | 6000 |  |  |  | 3300 | 179347.8261 | estimated | 21.5174 | Inventory (E above) | n M · P M · η M · Running: LF E, h E
mo-boilerhouse | Boiler feed pump and burner fan | Motors, pumps and fans | motors | electricity | 2 | 7.5 | output (shaft) | 0.904 | Running | 0.6 | 6500 |  |  |  | 3900 | 64712.3894 | estimated | 21.5174 | Inventory (E above) | n M · P M · η M · Running: LF E, h E
ph-burners | Tunnel oven burners (2 ovens) | Process heat | ovens | lpg | 2 | 400 | input | 1 | Baking | 0.42 | 5600 | Idle at temperature | 0.15 | 900 | 2487 | 1989600 | estimated | 20.3174 | Inventory (E above) | n M · P M · Baking: LF E, h E · Idle at temperature: LF E, h E
ph-oven-drives | Oven conveyors, recirculation and burner fans | Process heat | ovens | electricity | 2 | 18.5 | input | 1 | Running | 0.75 | 6500 |  |  |  | 4875 | 180375 | estimated | 21.4243 | Inventory (E above) | n M · P M · Running: LF E, h E
st-proofers | Proofers: humidification and heating | Steam and boilers | proofers | steam | 2 | 65 | input | 1 | In use | 0.6 | 6000 |  |  |  | 3600 | 468000 | estimated | 23.4521 | Inventory (E above) | n M · P C · In use: LF E, h E
st-washer | Crate and tray washer | Steam and boilers | washer | steam | 1 | 159 | input | 1 | In use | 0.5 | 4500 |  |  |  | 2250 | 357750 | estimated | 23.4521 | Inventory (E above) | n M · P C · In use: LF E, h E
st-calorifier | Calorifier: hot water for cleaning | Steam and boilers | hot-water | steam | 1 | 101 | input | 1 | In use | 0.45 | 5500 |  |  |  | 2475 | 249975 | estimated | 23.4521 | Inventory (E above) | n M · P C · In use: LF E, h E
lt-production | Production hall: twin 58 W T8 battens | Lighting | lighting | electricity | 160 | 0.13 | input | 1 | Lit | 1 | 6500 |  |  |  | 6500 | 135200 | estimated | 15.5885 | Inventory (E above) | n M · P M · Lit: LF M, h E
lt-warehouse | Warehouse and dispatch: 400 W metal-halide high bays | Lighting | lighting | electricity | 36 | 0.455 | input | 1 | Lit | 1 | 6000 |  |  |  | 6000 | 98280 | estimated | 15.5885 | Inventory (E above) | n M · P M · Lit: LF M, h E
lt-coldstore | Cold stores: twin 58 W T8 battens | Lighting | lighting | electricity | 40 | 0.13 | input | 1 | Lit | 1 | 8760 |  |  |  | 8760 | 45552 | estimated | 15.5885 | Inventory (E above) | n M · P M · Lit: LF M, h E
lt-offices | Offices and canteen: 4 × 18 W T8 troffers | Lighting | lighting | electricity | 90 | 0.08 | input | 1 | Lit | 1 | 2800 |  |  |  | 2800 | 20160 | estimated | 15.5885 | Inventory (E above) | n M · P M · Lit: LF M, h E
lt-external | External: 250 W sodium floodlights | Lighting | lighting | electricity | 18 | 0.28 | input | 1 | Lit | 1 | 4200 |  |  |  | 4200 | 21168 | estimated | 15.5885 | Inventory (E above) | n M · P M · Lit: LF M, h E
hv-splits | Office split units | HVAC and offices | hvac | electricity | 14 | 3.5 | input | 1 | Cooling | 0.55 | 2600 |  |  |  | 1430 | 70070 | estimated | 21.4243 | Inventory (E above) | n M · P M · Cooling: LF E, h E
hv-it | Servers and IT | HVAC and offices | hvac | electricity | 1 | 3 | input | 1 | Always on | 1 | 8760 |  |  |  | 8760 | 26280 | estimated | 15.5885 | Inventory (E above) | n M · P M · Always on: LF E, h M
hv-office | Canteen and office equipment | HVAC and offices | hvac | electricity | 1 | 25 | input | 1 | Office hours | 0.35 | 2800 |  |  |  | 980 | 24500 | estimated | 21.4243 | Inventory (E above) | n M · P M · Office hours: LF E, h E
Inventory total by carrier (every item, before system models or measured data replace any)
Carrier | Items | Σ E (kWh/yr)
electricity | 19 | 2937478.5237
lpg | 1 | 1989600
steam | 3 | 1075725

## Balance
Balance
Metered (bills) against bottom-up (inventory, system models, measured data) at each balance point. The remainder is shown as unaccounted, never forced (Sources & methods, section 5).
FICTIONAL DEMONSTRATION: Demo Foods (Pty) Ltd (fictional). Every name and number is invented.
Balance points: where a metered supply meets the estimated demand
Point | Balance point | Carrier | Metered supply (kWh/yr) | Bottom-up (kWh/yr) | Gap (kWh/yr) | Gap (% of metered) | ± of the gap (%) | Tolerance (±) | Status | Unaccounted (kWh/yr) | Lowest data level | What it means
elec-dist | Main LV boards | electricity | 2966404 | 2771775.5521 | 194628.4479 | 6.561% | 5.304 | 10% | Within tolerance | 194628.4479 | Level 2: equipment inventory | Remainder shown as unaccounted (not forced)
diesel | Diesel | diesel | 65216.6667 | 62941.1765 | 2275.4902 | 3.489% | 18.3498 | 10% | Within tolerance | 2275.4902 | Level 1: bills | Remainder shown as unaccounted (not forced)
lpg | LPG | lpg | 3902263.1389 | 3778311.7443 | 123951.3946 | 3.176% | 12.9022 | 10% | Within tolerance | 123951.3946 | Level 2: equipment inventory | Remainder shown as unaccounted (not forced)
site | Whole site (all carriers) | all | 6912483.8056 | 6591628.4728 | 320855.3327 | 4.642% |  |  |  | 320855.3327
Conversions: input = output ÷ η, loss = input − output
Node | Conversion | Efficiency η | η tag | Fixed output (kWh/yr) | Output (kWh/yr) | Input (kWh/yr) | Loss (kWh/yr) | Loss node
generator | Standby generator | 0.34 | assumed | 21400 | 21400 | 62941.1765 | 41541.1765 | gen-loss
boiler | Steam boiler | 0.8 | estimated |  | 1430969.3955 | 1788711.7443 | 357742.3489 | flue-loss
Flows: each link of the balance graph
Flow | From | To | Carrier | How it is worked out | Energy (kWh/yr) | Tag | ± (%) | Role
f-grid | grid | elec-dist | electricity | Metered (bills) | 2945004 | measured | 2 | normal
f-diesel | diesel | generator | diesel | Bottom-up | 62941.1765 | assumed | 18.0278 | normal
f-gen | generator | elec-dist | electricity | Fixed output (meter or log) | 21400 | estimated | 15 | normal
f-gen-loss | generator | gen-loss | heat | Conversion loss: input − output | 41541.1765 | assumed | 10 | loss
f-ca | elec-dist | ca | electricity | Bottom-up | 523716.1569 | estimated | 7.4441 | normal
f-refrig | elec-dist | refrig | electricity | Bottom-up | 857746.8714 | estimated | 12.3693 | normal
f-motors | elec-dist | motors | electricity | Bottom-up | 768727.5237 | estimated | 10.0644 | normal
f-ovens-el | elec-dist | ovens | electricity | Bottom-up | 180375 | estimated | 21.4243 | normal
f-lighting | elec-dist | lighting | electricity | Bottom-up | 320360 | estimated | 8.549 | normal
f-hvac | elec-dist | hvac | electricity | Bottom-up | 120850 | estimated | 13.589 | normal
f-lpg-ovens | lpg | ovens | lpg | Bottom-up | 1989600 | estimated | 20.3174 | normal
f-lpg-boiler | lpg | boiler | lpg | Bottom-up | 1788711.7443 | assumed | 13.9958 | normal
f-steam | boiler | steam-dist | steam | Bottom-up | 1418058.2048 | assumed | 13.5265 | normal
f-flue | boiler | flue-loss | heat | Conversion loss: input − output | 357742.3489 | estimated | 4 | loss
f-blowdown | boiler | blowdown | heat | Bottom-up | 12911.1907 | assumed | 50 | loss
f-proofers | steam-dist | proofers | steam | Bottom-up | 467615.9367 | estimated | 25.9808 | normal
f-washer | steam-dist | washer | steam | Bottom-up | 357206.6184 | estimated | 25.9808 | normal
f-hot-water | steam-dist | hot-water | steam | Bottom-up | 250044.6328 | estimated | 25.9808 | normal
f-traps | steam-dist | steam-traps | steam | Bottom-up | 178905.9477 | assumed | 46.4486 | loss
f-pipes | steam-dist | steam-pipes | steam | Bottom-up | 164285.0691 | estimated | 29.1548 | loss
flow:unaccounted:elec-dist | elec-dist | unaccounted:elec-dist | electricity | Unaccounted: metered − bottom-up | 194628.4479 | calculated | 80.8399 | unaccounted
flow:unaccounted:diesel | diesel | unaccounted:diesel | diesel | Unaccounted: metered − bottom-up | 2275.4902 | calculated | 525.9152 | unaccounted
flow:unaccounted:lpg | lpg | unaccounted:lpg | lpg | Unaccounted: metered − bottom-up | 123951.3946 | calculated | 406.1888 | unaccounted
Bottom-up terms: what each end use and loss is estimated from
Term | Description | Node | Carrier | Basis | Estimate (kWh/yr) | Scale (recorded) | Used (kWh/yr) | Tag | ± (%) | Source | Share of carrier
model:compressed-air | Compressor plant (2 × 61 kW, part-load model) | ca | electricity | model | 523716.1569 | 1 | 523716.1569 | estimated | 7.4441 | Compressed air model, worked out by the studio (Sources & methods, section 6)
measured:refrig | Refrigeration (interval data, annualised) | refrig | electricity | interval | 857746.8714 | 1 | 857746.8714 | estimated | 12.3693 | 16,450 kWh logged (336 readings at 30 min) × 52.14 (one week × 365/7)
item:mo-mixers | Dough mixers | motors | electricity | inventory | 173076.9231 | 1 | 173076.9231 | estimated | 21.5174 | E = n × P × Σ(LF × h) / η (Inventory sheet)
item:mo-fans | Oven-hall extraction fans | motors | electricity | inventory | 199949.2473 | 1 | 199949.2473 | estimated | 21.5174 | E = n × P × Σ(LF × h) / η (Inventory sheet)
item:mo-pumps | Cooling-water and process pumps | motors | electricity | inventory | 151641.1379 | 1 | 151641.1379 | estimated | 21.5174 | E = n × P × Σ(LF × h) / η (Inventory sheet)
item:mo-conveyors | Conveyors, dividers and moulders | motors | electricity | inventory | 179347.8261 | 1 | 179347.8261 | estimated | 21.5174 | E = n × P × Σ(LF × h) / η (Inventory sheet)
item:mo-boilerhouse | Boiler feed pump and burner fan | motors | electricity | inventory | 64712.3894 | 1 | 64712.3894 | estimated | 21.5174 | E = n × P × Σ(LF × h) / η (Inventory sheet)
item:ph-burners | Tunnel oven burners (2 ovens) | ovens | lpg | inventory | 1989600 | 1 | 1989600 | estimated | 20.3174 | E = n × P × Σ(LF × h) / η (Inventory sheet)
item:ph-oven-drives | Oven conveyors, recirculation and burner fans | ovens | electricity | inventory | 180375 | 1 | 180375 | estimated | 21.4243 | E = n × P × Σ(LF × h) / η (Inventory sheet)
item:lt-production | Production hall: twin 58 W T8 battens | lighting | electricity | inventory | 135200 | 1 | 135200 | estimated | 15.5885 | E = n × P × Σ(LF × h) / η (Inventory sheet)
item:lt-warehouse | Warehouse and dispatch: 400 W metal-halide high bays | lighting | electricity | inventory | 98280 | 1 | 98280 | estimated | 15.5885 | E = n × P × Σ(LF × h) / η (Inventory sheet)
item:lt-coldstore | Cold stores: twin 58 W T8 battens | lighting | electricity | inventory | 45552 | 1 | 45552 | estimated | 15.5885 | E = n × P × Σ(LF × h) / η (Inventory sheet)
item:lt-offices | Offices and canteen: 4 × 18 W T8 troffers | lighting | electricity | inventory | 20160 | 1 | 20160 | estimated | 15.5885 | E = n × P × Σ(LF × h) / η (Inventory sheet)
item:lt-external | External: 250 W sodium floodlights | lighting | electricity | inventory | 21168 | 1 | 21168 | estimated | 15.5885 | E = n × P × Σ(LF × h) / η (Inventory sheet)
item:hv-splits | Office split units | hvac | electricity | inventory | 70070 | 1 | 70070 | estimated | 21.4243 | E = n × P × Σ(LF × h) / η (Inventory sheet)
item:hv-it | Servers and IT | hvac | electricity | inventory | 26280 | 1 | 26280 | estimated | 15.5885 | E = n × P × Σ(LF × h) / η (Inventory sheet)
item:hv-office | Canteen and office equipment | hvac | electricity | inventory | 24500 | 1 | 24500 | estimated | 21.4243 | E = n × P × Σ(LF × h) / η (Inventory sheet)
model:steam:blowdown | Boiler blowdown (4% of feedwater) | blowdown | heat | model | 12911.1907 | 1 | 12911.1907 | assumed | 50 | Steam and boilers model, worked out by the studio (Sources & methods, section 6)
model:steam:st-proofers | Proofers: humidification and heating | proofers | steam | model | 467615.9367 | 1 | 467615.9367 | estimated | 25.9808 | Steam and boilers model, worked out by the studio (Sources & methods, section 6)
model:steam:st-washer | Crate and tray washer | washer | steam | model | 357206.6184 | 1 | 357206.6184 | estimated | 25.9808 | Steam and boilers model, worked out by the studio (Sources & methods, section 6)
model:steam:st-calorifier | Calorifier: hot water for cleaning | hot-water | steam | model | 250044.6328 | 1 | 250044.6328 | estimated | 25.9808 | Steam and boilers model, worked out by the studio (Sources & methods, section 6)
model:steam:traps | Failed steam traps (6 open, Napier orifice estimate) | steam-traps | steam | model | 125401.3652 | 1 | 125401.3652 | assumed | 64.0312 | Steam and boilers model, worked out by the studio (Sources & methods, section 6)
model:steam:leaks | Steam leaks (2 small, Napier orifice estimate) | steam-traps | steam | model | 53504.5825 | 1 | 53504.5825 | estimated | 40 | Steam and boilers model, worked out by the studio (Sources & methods, section 6)
model:steam:pipes | Bare pipe and valves (42 m) | steam-pipes | steam | model | 164285.0691 | 1 | 164285.0691 | estimated | 29.1548 | Steam and boilers model, worked out by the studio (Sources & methods, section 6)
Nodes by carrier: bottom-up terms, the inventory's estimate, inflow and outflow
Node | Name | Kind | System | Data level | Carrier | Basis | Bottom-up terms (kWh/yr) | Inventory estimate (kWh/yr) | Inflow (kWh/yr) | Outflow (kWh/yr)
grid | Grid electricity | source | Electrical supply and tariff | 1 | electricity | bills |  |  | 2945004 | 2945004
diesel | Diesel | source |  | 1 | diesel | bills |  |  | 65216.6667 | 65216.6667
lpg | LPG | source |  | 1 | lpg | bills |  |  | 3902263.1389 | 3902263.1389
generator | Standby generator | conversion | Electrical supply and tariff | 1 | diesel | flows |  |  | 62941.1765 | 0
generator | Standby generator | conversion | Electrical supply and tariff | 1 | electricity | flows |  |  | 0 | 21400
generator | Standby generator | conversion | Electrical supply and tariff | 1 | heat | flows |  |  | 0 | 41541.1765
gen-loss | Generator losses | loss | Electrical supply and tariff | 1 | heat | flows | 0 |  | 41541.1765 | 0
elec-dist | Main LV boards | distribution | Electrical supply and tariff | 1 | electricity | flows |  |  | 2966404 | 2966404
ca | Compressed air | end-use | Compressed air | 2 | electricity | model | 523716.1569 | 641232 | 523716.1569 | 0
refrig | Refrigeration | end-use | Refrigeration and chillers | 3 | electricity | interval | 857746.8714 | 905934 | 857746.8714 | 0
motors | Motors, pumps and fans | end-use | Motors, pumps and fans | 2 | electricity | inventory | 768727.5237 | 768727.5237 | 768727.5237 | 0
ovens | Tunnel ovens | end-use | Process heat | 2 | electricity | inventory | 180375 | 180375 | 180375 | 0
ovens | Tunnel ovens | end-use | Process heat | 2 | lpg | inventory | 1989600 | 1989600 | 1989600 | 0
lighting | Lighting | end-use | Lighting | 2 | electricity | inventory | 320360 | 320360 | 320360 | 0
hvac | HVAC and offices | end-use | HVAC and offices | 2 | electricity | inventory | 120850 | 120850 | 120850 | 0
boiler | Steam boiler | conversion | Steam and boilers | 2 | lpg | flows |  |  | 1788711.7443 | 0
boiler | Steam boiler | conversion | Steam and boilers | 2 | steam | flows |  |  | 0 | 1418058.2048
boiler | Steam boiler | conversion | Steam and boilers | 2 | heat | flows |  |  | 0 | 370653.5395
flue-loss | Boiler flue and shell losses | loss | Steam and boilers | 2 | heat | flows | 0 |  | 357742.3489 | 0
blowdown | Boiler blowdown | loss | Steam and boilers | 2 | heat | model | 12911.1907 |  | 12911.1907 | 0
steam-dist | Steam mains | distribution | Steam and boilers | 2 | steam | flows |  |  | 1418058.2048 | 1418058.2048
proofers | Proofers | end-use | Steam and boilers | 2 | steam | model | 467615.9367 | 468000 | 467615.9367 | 0
washer | Crate washer | end-use | Steam and boilers | 2 | steam | model | 357206.6184 | 357750 | 357206.6184 | 0
hot-water | Hot water (calorifier) | end-use | Steam and boilers | 2 | steam | model | 250044.6328 | 249975 | 250044.6328 | 0
steam-traps | Failed traps and steam leaks | loss | Steam and boilers | 2 | steam | model | 178905.9477 |  | 178905.9477 | 0
steam-pipes | Bare pipe heat loss | loss | Steam and boilers | 2 | steam | model | 164285.0691 |  | 164285.0691 | 0
unaccounted:elec-dist | Unaccounted electricity | unaccounted |  | 2 | electricity | flows | 0 |  | 194628.4479 | 0
unaccounted:diesel | Unaccounted diesel | unaccounted |  | 1 | diesel | flows | 0 |  | 2275.4902 | 0
unaccounted:lpg | Unaccounted lpg | unaccounted |  | 2 | lpg | flows | 0 |  | 123951.3946 | 0

## Measures
Measures
Each measure as the business case reads it (lib/ecosystem MeasureResult): savings by carrier and by tariff component, costs, life and tags.
FICTIONAL DEMONSTRATION: Demo Foods (Pty) Ltd (fictional). Every name and number is invented.
# | Measure | Measure id | System | Category | Source module | Opportunity status | Electricity saved (kWh/yr) | LPG saved (kWh/yr) | Energy saved, total (kWh/yr) | kWh tag | Demand reduction (kVA) | Energy charges saved (R/yr) | Demand charges saved (R/yr) | Capacity charges saved (R/yr) | Fixed charges saved (R/yr) | Gross saving, year 1 (R/yr) | Rand tag | Saving decay (fraction/yr) | Capex (R) | Capex tag | Running cost change (R/yr) | Running cost tag | Life (years) | Life tag | Months to implement | Measure tag | Rand saving priced
1 | Switch compressors off outside production | m-o-ca-off-hours | Compressed air | Behaviour and management | audit-compressed-air 1.0.0 | quantified | 73358.3372 | 0 | 73358.3372 | estimated | 0 | 109789.3214 | 0 | 0 | 0 | 109789.3214 | estimated | 0 | 15000 | assumed | 0 | assumed | 5 | assumed | 1 | assumed | energy at the bill rates (Inputs)
2 | Compressed-air leak repair programme | m-o-ca-leaks | Compressed air | Maintenance | audit-compressed-air 1.0.0 | quantified | 130133.0127 | 0 | 130133.0127 | estimated | 0 | 194759.2556 | 0 | 0 | 0 | 194759.2556 | estimated | 0 | 45000 | assumed | 24000 | assumed | 5 | assumed | 2 | assumed | energy at the bill rates (Inputs)
3 | Duct the compressor intakes to outside air | m-o-ca-intake | Compressed air | Retrofit | audit-compressed-air 1.0.0 | quantified | 14691.6182 | 0 | 14691.6182 | assumed | 0 | 21987.7229 | 0 | 0 | 0 | 21987.7229 | assumed | 0 | 36000 | assumed | 0 | assumed | 15 | assumed | 2 | assumed | energy at the bill rates (Inputs)
4 | Variable-speed trim compressor | m-o-ca-vsd | Compressed air | New technology | audit-compressed-air 1.0.0 | quantified | 11578.7716 | 0 | 11578.7716 | assumed | 0 | 17328.9843 | 0 | 0 | 0 | 17328.9843 | assumed | 0 | 518500 | assumed | 0 | assumed | 15 | assumed | 4 | assumed | energy at the bill rates (Inputs)
5 | Variable-speed drive on a throttled pump (pump and system curves): Cooling-water and process pumps | m-o-mo-pump-vsd-mo-pumps | Motors, pumps and fans | Retrofit | audit-pump-system 1.0.0 | quantified | 49819.5882 | 0 | 49819.5882 | assumed | 0 | 74560.8337 | 0 | 0 | 0 | 74560.8337 | assumed | 0 | 82500 | assumed | 825 | assumed | 10 | assumed | 2 | assumed | energy at the bill rates (Inputs)
6 | VSDs on the oven-hall extraction fans (2 × 22 kW) | m-o-mo-vsd-mo-fans | Motors, pumps and fans | Retrofit | motor-vsd-savings 1.0.0 | quantified | 87944.1038 | 0 | 87944.1038 | calculated | 0 | 131618.6249 | 0 | 0 | 0 | 131618.6249 | calculated | 0 | 98000 | estimated | 1000 | assumed | 10 | assumed | 2 | assumed | energy at the bill rates (Inputs)
7 | Synchronous or cogged belts instead of V-belts: Oven-hall extraction fans | m-o-mo-belt-drive-mo-fans | Motors, pumps and fans | Retrofit | audit-belt-drive 1.0.0 | quantified | 5714.5481 | 0 | 5714.5481 | assumed | 0 | 8552.4889 | 0 | 0 | 0 | 8552.4889 | assumed | 0 | 19800 | assumed | 0 | assumed | 10 | assumed | 1 | assumed | energy at the bill rates (Inputs)
8 | Floating head pressure on the refrigeration plant | m-o-rf-head-pressure | Refrigeration and chillers | Controls | audit-refrigeration 1.0.0 | quantified | 91044.9802 | 0 | 91044.9802 | estimated | 0 | 136259.4487 | 0 | 0 | 0 | 136259.4487 | estimated | 0 | 130000 | assumed | 0 | assumed | 10 | assumed | 3 | assumed | energy at the bill rates (Inputs)
9 | Refrigeration heat recovery: a desuperheater for hot water | m-o-rf-desuperheater | Refrigeration and chillers | Heat recovery | audit-heat-exchange 1.0.0 | quantified | 0 | 126494.1142 | 126494.1142 | assumed | 0 | 235872.7458 | 0 | 0 | 0 | 235872.7458 | assumed | 0 | 200297.4294 | assumed | 0 | assumed | 15 | assumed | 3 | assumed | energy at the bill rates (Inputs)
10 | Boiler combustion tuning and O2 trim | m-o-st-combustion | Steam and boilers | Controls | audit-steam 1.0.0 | quantified | 0 | 85176.7497 | 85176.7497 | assumed | 0 | 158828.527 | 0 | 0 | 0 | 158828.527 | assumed | 0 | 85000 | assumed | 8000 | assumed | 10 | assumed | 2 | assumed | energy at the bill rates (Inputs)
11 | Steam trap survey and repair | m-o-st-traps | Steam and boilers | Maintenance | audit-steam 1.0.0 | quantified | 0 | 140505.3366 | 140505.3366 | assumed | 0 | 261999.3803 | 0 | 0 | 0 | 261999.3803 | assumed | 0 | 42000 | assumed | 15000 | assumed | 5 | assumed | 1 | assumed | energy at the bill rates (Inputs)
12 | Repair steam leaks | m-o-st-leaks | Steam and boilers | Maintenance | audit-steam 1.0.0 | quantified | 0 | 59948.9436 | 59948.9436 | assumed | 0 | 111786.4023 | 0 | 0 | 0 | 111786.4023 | assumed | 0 | 7000 | assumed | 0 | assumed | 3 | assumed | 1 | assumed | energy at the bill rates (Inputs)
13 | Insulate bare steam pipe, valves and flanges | m-o-st-insulation | Steam and boilers | Retrofit | audit-steam 1.0.0 | quantified | 0 | 181729.5947 | 181729.5947 | assumed | 0 | 338869.9842 | 0 | 0 | 0 | 338869.9842 | assumed | 0 | 67200 | assumed | 0 | assumed | 20 | assumed | 1 | assumed | energy at the bill rates (Inputs)
14 | Heat pump instead of steam for hot water | m-o-st-heat-pump | Steam and boilers | New technology | audit-heat-pump 1.0.0 | quantified | -65135.2834 | 298807.5878 | 233672.3044 | assumed | 0 | 459701.9899 | 0 | 0 | 0 | 459701.9899 | assumed | 0 | 769780.6215 | assumed | 0 | assumed | 15 | assumed | 4 | assumed | energy at the bill rates (Inputs)
15 | Return more condensate | m-o-st-condensate | Steam and boilers | Heat recovery | audit-steam 1.0.0 | quantified | 0 | 41786.3856 | 41786.3856 | assumed | 0 | 77918.7993 | 0 | 0 | 0 | 77918.7993 | assumed | 0 | 250000 | assumed | -22270.5248 | estimated | 15 | assumed | 4 | assumed | energy at the bill rates (Inputs)
16 | Flue-gas economiser | m-o-st-economiser | Steam and boilers | Heat recovery | audit-economiser 1.0.0 | quantified | 0 | 78640.177 | 78640.177 | assumed | 0 | 146639.8227 | 0 | 0 | 0 | 146639.8227 | assumed | 0 | 176634.9126 | assumed | 0 | assumed | 20 | assumed | 4 | assumed | energy at the bill rates (Inputs)
17 | Tune the burners on ovens, fryers and dryers: Tunnel oven burners (2 ovens) | m-o-ph-burner-tuning-ph-burners | Process heat | Controls | audit-burner-tuning 1.0.0 | quantified | 0 | 155940.7626 | 155940.7626 | assumed | 0 | 290781.718 | 0 | 0 | 0 | 290781.718 | assumed | 0 | 13000 | assumed | 8000 | assumed | 5 | assumed | 1 | assumed | energy at the bill rates (Inputs)
18 | Insulate the crate washer's soak tank and fit a lid | m-o-ph-hot-surfaces | Process heat | Retrofit | audit-hot-surfaces 1.0.0 | quantified | 0 | 29200.8719 | 29200.8719 | assumed | 0 | 54450.6744 | 0 | 0 | 0 | 54450.6744 | assumed | 0 | 10950 | assumed | 0 | assumed | 15 | assumed | 1 | assumed | energy at the bill rates (Inputs)
19 | Recover oven flue heat: Tunnel oven burners (2 ovens) | m-o-ph-oven-heat-recovery-ph-burners | Process heat | Heat recovery | audit-oven-heat-recovery 1.0.0 | quantified | 0 | 63264.0118 | 63264.0118 | assumed | 0 | 117967.9882 | 0 | 0 | 0 | 117967.9882 | assumed | 0 | 248410.8693 | assumed | 0 | assumed | 15 | assumed | 4 | assumed | energy at the bill rates (Inputs)
20 | Widen HVAC set points | m-o-hv-setpoints | HVAC and offices | Behaviour and management | audit-hvac 1.0.0 | quantified | 4204.2 | 0 | 4204.2 | assumed | 0 | 6292.0764 | 0 | 0 | 0 | 6292.0764 | assumed | 0 | 5600 | assumed | 0 | assumed | 5 | assumed | 1 | assumed | energy at the bill rates (Inputs)
21 | Occupancy sensors in intermittently used areas | m-o-lt-occupancy | Lighting | Controls | audit-lighting 1.0.0 | quantified | 34519.68 | 0 | 34519.68 | assumed | 0 | 51662.7337 | 0 | 0 | 0 | 51662.7337 | assumed | 0 | 14000 | assumed | 0 | assumed | 10 | assumed | 1 | assumed | energy at the bill rates (Inputs)
22 | LED lighting retrofit | m-o-lt-led | Lighting | Retrofit | audit-lighting 1.0.0 | quantified | 168233.92 | 0 | 168233.92 | estimated | 0 | 251781.7143 | 0 | 0 | 0 | 251781.7143 | estimated | 0 | 511600 | assumed | 0 | assumed | 10 | assumed | 2 | assumed | energy at the bill rates (Inputs)
23 | Run on fewer transformers at light load | m-o-el-transformer-standby | Electrical supply and tariff | Controls | audit-transformer 1.0.0 | quantified | 5400.8727 | 0 | 5400.8727 | calculated | 0 | 8083.037 | 0 | 0 | 0 | 8083.037 | calculated | 0 | 15000 | assumed | 0 | assumed | 10 | assumed | 1 | assumed | energy at the bill rates (Inputs)
24 | Power-factor correction | m-o-el-pf | Electricity supply: kVA demand and capacity | Retrofit | power-factor-correction 1.0.0 | quantified | 0 | 0 | 0 |  | 69.4667 | 0 | 35011.1942 | 0 | 0 | 35011.1942 | calculated | 0 | 136000 | estimated | 1400 | assumed | 15 | assumed | 2 | assumed | demand: kVA × demand rate × 12
Sources and notes, measure by measure
# | Measure | Sources and notes
1 | Switch compressors off outside production | Saving: 73,358 kWh electricity × R1.50/kWh ¦ Capex: 1 installation × R15,000 (Compressor timer or sequencer setting and an isolation valve: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Behaviour change held by a timer (assumed) ¦ A sanitation or maintenance crew may still need air on some idle days; the share switched off allows for it. ¦ Any fall in the billed maximum demand is not counted.
2 | Compressed-air leak repair programme | Saving: 130,133 kWh electricity × R1.50/kWh ¦ Capex: 1 installation × R45,000 (Ultrasonic leak survey, tags, fittings and labour for the first repair round: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: 1 programme a year × R24,000 (Quarterly ultrasonic leak survey and repairs: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Life: Programme horizon (assumed) ¦ Leaks come back: the quarterly survey in the running cost keeps the rate at the target. ¦ Sequenced: worked out after Switch compressors off outside production. ¦ On its own it would save 155,241 kWh a year. ¦ Any fall in the billed maximum demand is not counted.
3 | Duct the compressor intakes to outside air | Saving: 14,692 kWh electricity × R1.50/kWh ¦ Capex: 2 compressors × R18,000 (Intake duct from a compressor to outside air, with a filter, weather hood and damper: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Ductwork life (assumed) ¦ Use the year's average at the intake and outside (a week of logging at both, set against the weather station), not one hot afternoon. ¦ Keep the duct short and fit a filter and a weather hood; a damper can switch back to room air if the room needs the heat. ¦ Sequenced: worked out after Switch compressors off outside production; Compressed-air leak repair programme. ¦ On its own it would save 24,028 kWh a year. ¦ Any fall in the billed maximum demand is not counted.
4 | Variable-speed trim compressor | Saving: 11,579 kWh electricity × R1.50/kWh ¦ Capex: 61 kW of compressor input × R8,500 (Variable-speed screw compressor (trim unit), installed: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Compressor life (assumed) ¦ VSD curve: typical shape (assumed); the maker's CAGI data sheet replaces it. ¦ Right-size the trim unit after leaks are fixed: a smaller VSD may do. ¦ Sequenced: worked out after Switch compressors off outside production; Compressed-air leak repair programme; Duct the compressor intakes to outside air. ¦ On its own it would save 59,002 kWh a year. ¦ Any fall in the billed maximum demand is not counted.
5 | Variable-speed drive on a throttled pump (pump and system curves): Cooling-water and process pumps | Saving: 49,820 kWh electricity × R1.50/kWh ¦ Capex: 33 kW of motor rating × R2,500 (Variable-speed drive for a pump or fan, fitted: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: Drive upkeep: 1% of capex a year (as the VSD tool) ¦ Life: Drive life (assumed, as the VSD tool) ¦ Motor efficiency is held at its full-load value; the drive's own losses are included. ¦ The pump's curve from the maker, and suction and discharge pressures at two flows, firm up the static head and the margin the valve burns. ¦ Any fall in the billed maximum demand is not counted.
6 | VSDs on the oven-hall extraction fans (2 × 22 kW) | Saving: 87,944 kWh × R1.50/kWh ¦ Capex: Installer quote for two 22 kW drives, fitted (fictional) ¦ Running cost: Default: 1% of capex a year ¦ Life: Default life for a drive ¦ Screening estimate: motor part-load efficiency, minimum speed and pump-curve shifts are ignored. ¦ Sequenced: worked out after Variable-speed drive on a throttled pump (pump and system curves): Cooling-water and process pumps. ¦ On its own it would save 87,944 kWh a year.
7 | Synchronous or cogged belts instead of V-belts: Oven-hall extraction fans | Saving: 5,715 kWh electricity × R1.50/kWh ¦ Capex: 44 kW of motor rating × R450 (Synchronous belt and sprockets, supplied: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Sprockets last; replacement belts cost about the same as V-belts (assumed) ¦ A synchronous belt does not slip, so the fan or pump runs a little faster on the same pulleys and can use more power: change the pulley ratio, or trim the speed on its VSD, to hold the old speed. ¦ Sequenced: worked out after Variable-speed drive on a throttled pump (pump and system curves): Cooling-water and process pumps; VSDs on the oven-hall extraction fans (2 × 22 kW). ¦ On its own it would save 10,201 kWh a year. ¦ Any fall in the billed maximum demand is not counted.
8 | Floating head pressure on the refrigeration plant | Saving: 91,045 kWh electricity × R1.50/kWh ¦ Capex: 2 circuits × R65,000 (Floating head pressure: controller changes and electronic expansion valves: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Controls life (assumed) ¦ The achievable condensing temperature depends on ambient and the condenser approach; a year of weather data firms it up. ¦ Any fall in the billed maximum demand is not counted.
9 | Refrigeration heat recovery: a desuperheater for hot water | Saving: 126,494 kWh lpg × R1.86/kWh ¦ Capex: 53.4 kW of desuperheat duty × R3,750 (Desuperheater on the compressor discharge, with water piping, pump and controls, supplied: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Exchanger life (assumed) ¦ Floating head pressure lowers the discharge temperature: confirm the water temperature the desuperheater can reach. ¦ Not netted against other measures that make the same hot water: count one of them. ¦ Sequenced: worked out after Floating head pressure on the refrigeration plant. ¦ On its own it would save 132,184 kWh a year. ¦ Any fall in the billed maximum demand is not counted.
10 | Boiler combustion tuning and O2 trim | Saving: 85,177 kWh lpg × R1.86/kWh ¦ Capex: 1 boiler × R85,000 (O₂ trim kit, commissioning and burner tuning: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: 1 boiler a year × R8,000 (Annual combustion test and re-tune: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Life: Controls life (assumed) ¦ Any fall in the billed maximum demand is not counted.
11 | Steam trap survey and repair | Saving: 140,505 kWh lpg × R1.86/kWh ¦ Capex: 1 survey × R15,000 (Steam trap survey (first): assumed placeholder 2026 budget — replace with supplier quotes) + 6 traps × R4,500 (Steam trap replaced, fitted: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: 1 programme a year × R15,000 (Annual steam trap survey: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Life: Trap life with an annual survey (assumed) ¦ Sequenced: worked out after Boiler combustion tuning and O2 trim. ¦ On its own it would save 147,531 kWh a year. ¦ Any fall in the billed maximum demand is not counted.
12 | Repair steam leaks | Saving: 59,949 kWh lpg × R1.86/kWh ¦ Capex: 2 leaks × R3,500 (Steam leak repair: gland repacking, gasket or union, fitted: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Repairs hold about three years before glands and gaskets need doing again (assumed) ¦ Leak sizes are judged by eye: a small wisp is taken as a 1.6 mm hole, a medium plume 3.2 mm and a large jet 6.4 mm. An ultrasonic survey firms them up. ¦ Sequenced: worked out after Boiler combustion tuning and O2 trim; Steam trap survey and repair. ¦ On its own it would save 62,946 kWh a year. ¦ Any fall in the billed maximum demand is not counted.
13 | Insulate bare steam pipe, valves and flanges | Saving: 181,730 kWh lpg × R1.86/kWh ¦ Capex: 42 m of pipe × R1,600 (Pipe insulation with cladding, installed (DN25-DN50; valves as equivalent length): assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Insulation life (assumed) ¦ Sequenced: worked out after Boiler combustion tuning and O2 trim; Steam trap survey and repair; Repair steam leaks. ¦ On its own it would save 190,816 kWh a year. ¦ Any fall in the billed maximum demand is not counted.
14 | Heat pump instead of steam for hot water | Saving: 298,808 kWh lpg × R1.86/kWh + -65,135 kWh electricity × R1.50/kWh ¦ Capex: 79.0 kW of heating capacity × R9,750 (Air-to-water heat pump for hot water up to about 65 °C, with storage, supplied: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Heat pump life (assumed) ¦ The heat pump adds about 26 kW of electrical load; if it runs at the time of the monthly maximum demand, the demand charge rises (not counted). ¦ Confirm the hot-water temperature: above about 65 °C use a high-temperature heat pump or keep steam for the top-up (coverage below 100%). ¦ Sequenced: worked out after Boiler combustion tuning and O2 trim; Steam trap survey and repair; Repair steam leaks; Insulate bare steam pipe, valves and flanges. ¦ On its own it would save 248,613 kWh a year. ¦ Any fall in the billed maximum demand is not counted.
15 | Return more condensate | Saving: 41,786 kWh lpg × R1.86/kWh ¦ Capex: 1 installation × R250,000 (Condensate pump set, flash vessel and return piping: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: 464 m³ less make-up water × R48/m³ (water, effluent and treatment) ¦ Life: Pumps and piping life (assumed) ¦ The condensate pump's electricity is not deducted (small next to the fuel saved). ¦ Sequenced: worked out after Boiler combustion tuning and O2 trim; Steam trap survey and repair; Repair steam leaks; Insulate bare steam pipe, valves and flanges; Heat pump instead of steam for hot water. ¦ On its own it would save 64,954 kWh a year. ¦ Any fall in the billed maximum demand is not counted.
16 | Flue-gas economiser | Saving: 78,640 kWh lpg × R1.86/kWh ¦ Capex: 22.1 kW of design heat recovery × R7,980 (Feedwater economiser with bypass and controls, supplied: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Economiser life (assumed) ¦ Worked out on the flue gas after O₂ trim (less excess air, so less flue gas to cool). ¦ Feedwater leaves the economiser at about 115 °C (in at 69 °C). ¦ Sequenced: worked out after Boiler combustion tuning and O2 trim; Steam trap survey and repair; Repair steam leaks; Insulate bare steam pipe, valves and flanges; Heat pump instead of steam for hot water; Return more condensate. ¦ On its own it would save 195,345 kWh a year. ¦ Any fall in the billed maximum demand is not counted.
17 | Tune the burners on ovens, fryers and dryers: Tunnel oven burners (2 ovens) | Saving: 155,941 kWh lpg × R1.86/kWh ¦ Capex: 2 burners × R6,500 (Burner tuning with a combustion analyser: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: 2 burner a year × R4,000 (Yearly re-tune: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Life: Held by a yearly re-tune (assumed) ¦ Agree the target O₂ with the burner's maker (some oven burners need more air); keep CO below about 100 ppm. ¦ Tuning leaves 40% less flue gas per kg of fuel; a flue heat recovery on this oven is worked out after the tuning, so the two do not overlap. ¦ Any fall in the billed maximum demand is not counted.
18 | Insulate the crate washer's soak tank and fit a lid | Saving: 29,201 kWh lpg × R1.86/kWh ¦ Capex: 6 m² of surface × R1,200 (Insulation with cladding on hot tanks and equipment, installed: assumed placeholder 2026 budget — replace with supplier quotes) + 1.50 m² of open surface × R2,500 (Insulated lid or cover for an open hot tank, fitted: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Insulation and lids (assumed) ¦ Bare areas are taken as walls; a top loses about 15% more by convection, so the saving there is a little understated. ¦ Evaporation is from the pool equation (ASHRAE), fitted to pools: confirm on a hot tank by the fall in level, or the make-up water, with the lid off and on. ¦ Not netted against the steam measures (they change the boiler fuel behind each kWh of steam heat): noted, not counted twice. ¦ Any fall in the billed maximum demand is not counted.
19 | Recover oven flue heat: Tunnel oven burners (2 ovens) | Saving: 63,264 kWh lpg × R1.86/kWh ¦ Capex: 27.6 kW of design heat recovery × R9,000 (Oven or dryer flue-gas heat recovery: cleanable exchanger, ducting, bypass damper and controls, supplied: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Exchanger and ducting life (assumed) ¦ Sized for 27.6 kW at full firing. Oven flue gas carries baking vapour and fat: specify a bypass and cleaning access. ¦ Displaces the oven's own fuel by default; if the hot water would otherwise come from steam or a heat pump, the saving overlaps with those measures: count one of them. ¦ Worked out after the burner tuning on this oven (4.0% O₂, 1,833,659 kWh/yr of fuel), so the two measures do not count the same fuel twice. ¦ The flue test (2026-08-20) is applied to all 2 units of this register line: test each before sizing. ¦ Any fall in the billed maximum demand is not counted.
20 | Widen HVAC set points | Saving: 4,204 kWh electricity × R1.50/kWh ¦ Capex: 14 units × R400 (Set-point limits on the unit controllers (lock-out or BMS), per unit: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Behaviour change held by controller limits (assumed) ¦ Agree the new set points with the occupants and hold them with controller limits, or the saving drifts back. ¦ Any fall in the billed maximum demand is not counted.
21 | Occupancy sensors in intermittently used areas | Saving: 34,520 kWh electricity × R1.50/kWh ¦ Capex: 10 sensors × R1,400 (Occupancy sensor, installed (one per 8 fittings): assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Sensor life (assumed) ¦ LED fittings tolerate frequent switching; with discharge lamps fit the sensors after the LED retrofit. ¦ Any fall in the billed maximum demand is not counted.
22 | LED lighting retrofit | Saving: 168,234 kWh electricity × R1.50/kWh ¦ Capex: 160 luminaires × R1,100 (LED batten or troffer replacing fluorescent, fitted: assumed placeholder 2026 budget — replace with supplier quotes) + 36 luminaires × R3,450 (LED high bay replacing metal-halide or sodium, fitted: quote, Fictional Lighting Supplies (Pty) Ltd, 2026-09-15) + 40 luminaires × R1,100 (LED batten or troffer replacing fluorescent, fitted: assumed placeholder 2026 budget — replace with supplier quotes) + 90 luminaires × R1,100 (LED batten or troffer replacing fluorescent, fitted: assumed placeholder 2026 budget — replace with supplier quotes) + 18 luminaires × R3,800 (LED floodlight replacing metal-halide or sodium outdoors, fitted: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: 50,000 h rated life (L70) at each area's hours, capped at 15 years (assumed) ¦ Same light level assumed; confirm with a lighting design for high bays. ¦ Sequenced: worked out after Occupancy sensors in intermittently used areas. ¦ On its own it would save 189,736 kWh a year. ¦ Any fall in the billed maximum demand is not counted.
23 | Run on fewer transformers at light load | Saving: 5,401 kWh electricity × R1.50/kWh ¦ Capex: 1 installation × R15,000 (Switching procedure, protection check and interlock to run on fewer transformers: assumed placeholder 2026 budget — replace with supplier quotes) ¦ Running cost: No change in running costs (assumed) ¦ Life: Operating procedure (assumed) ¦ Keep the unit switched off as a cold standby: the site keeps a spare, with a changeover time instead of automatic cover. Check protection, earthing and the changeover procedure with the unit isolated. ¦ These losses are inside the metered energy when the site is metered on the medium-voltage side; on a low-voltage meter the utility carries them and nothing is saved on the bill. ¦ Any fall in the billed maximum demand is not counted.
24 | Power-factor correction | Saving: No energy saving counted ¦ Capex: 200 kvar × R680/kvar (power-factor tool) ¦ Running cost: Default: 1% of capex a year ¦ Life: Default life for a capacitor bank ¦ Counts kVA-based charges only; reactive energy (kvarh) charges and lower cable losses are not added. ¦ Assumes the kW and power factor at maximum demand are similar every month.

## CashFlows
CashFlows
Nominal rand, end-of-year flows, year 0 = now. CF0 = −capex; CFt = S(1 − d)^(t−1)(1 + e)^(t−1) − O(1 + e)^(t−1) for t ≤ n, 0 after (lib/ecosystem/portfolio.ts).
FICTIONAL DEMONSTRATION: Demo Foods (Pty) Ltd (fictional). Every name and number is invented.
# | Measure | Life n (years) | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| Escalation factor (1 + e)^(t − 1) |  |  | 1 | 1.08 | 1.1664 | 1.2597 | 1.3605 | 1.4693 | 1.5869 | 1.7138 | 1.8509 | 1.999 | 2.1589 | 2.3316 | 2.5182 | 2.7196 | 2.9372 | 3.1722 | 3.4259 | 3.7 | 3.996 | 4.3157
| Discount factor 1 ÷ (1 + r)^t |  | 1 | 0.89286 | 0.79719 | 0.71178 | 0.63552 | 0.56743 | 0.50663 | 0.45235 | 0.40388 | 0.36061 | 0.32197 | 0.28748 | 0.25668 | 0.22917 | 0.20462 | 0.1827 | 0.16312 | 0.14564 | 0.13004 | 0.11611 | 0.10367
1 | Switch compressors off outside production | 5 | -15000 | 109789.3214 | 118572.4671 | 128058.2644 | 138302.9256 | 149367.1596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Compressed-air leak repair programme | 5 | -45000 | 170759.2556 | 184419.996 | 199173.5957 | 215107.4834 | 232316.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Duct the compressor intakes to outside air | 15 | -36000 | 21987.7229 | 23746.7408 | 25646.48 | 27698.1984 | 29914.0543 | 32307.1786 | 34891.7529 | 37683.0932 | 40697.7406 | 43953.5599 | 47469.8447 | 51267.4322 | 55368.8268 | 59798.333 | 64582.1996 | 0 | 0 | 0 | 0 | 0
4 | Variable-speed trim compressor | 15 | -518500 | 17328.9843 | 18715.303 | 20212.5273 | 21829.5295 | 23575.8918 | 25461.9632 | 27498.9202 | 29698.8339 | 32074.7406 | 34640.7198 | 37411.9774 | 40404.9356 | 43637.3304 | 47128.3169 | 50898.5822 | 0 | 0 | 0 | 0 | 0
5 | Variable-speed drive on a throttled pump (pump and system curves): Cooling-water and process pumps | 10 | -82500 | 73735.8337 | 79634.7004 | 86005.4764 | 92885.9145 | 100316.7877 | 108342.1307 | 117009.5012 | 126370.2613 | 136479.8822 | 147398.2728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | VSDs on the oven-hall extraction fans (2 × 22 kW) | 10 | -98000 | 130618.6249 | 141068.1149 | 152353.564 | 164541.8492 | 177705.1971 | 191921.6129 | 207275.3419 | 223857.3692 | 241765.9588 | 261107.2355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Synchronous or cogged belts instead of V-belts: Oven-hall extraction fans | 10 | -19800 | 8552.4889 | 9236.688 | 9975.623 | 10773.6729 | 11635.5667 | 12566.412 | 13571.725 | 14657.463 | 15830.06 | 17096.4648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Floating head pressure on the refrigeration plant | 10 | -130000 | 136259.4487 | 147160.2046 | 158933.021 | 171647.6627 | 185379.4757 | 200209.8337 | 216226.6204 | 233524.7501 | 252206.7301 | 272383.2685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Refrigeration heat recovery: a desuperheater for hot water | 15 | -200297.4294 | 235872.7458 | 254742.5654 | 275121.9707 | 297131.7283 | 320902.2666 | 346574.4479 | 374300.4037 | 404244.436 | 436583.9909 | 471510.7102 | 509231.567 | 549970.0924 | 593967.6998 | 641485.1158 | 692803.925 | 0 | 0 | 0 | 0 | 0
10 | Boiler combustion tuning and O2 trim | 10 | -85000 | 150828.527 | 162894.8091 | 175926.3939 | 190000.5054 | 205200.5458 | 221616.5895 | 239345.9166 | 258493.59 | 279173.0772 | 301506.9233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Steam trap survey and repair | 5 | -42000 | 246999.3803 | 266759.3307 | 288100.0772 | 311148.0834 | 336039.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Repair steam leaks | 3 | -7000 | 111786.4023 | 120729.3144 | 130387.6596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | Insulate bare steam pipe, valves and flanges | 20 | -67200 | 338869.9842 | 365979.5829 | 395257.9495 | 426878.5855 | 461028.8723 | 497911.1821 | 537744.0767 | 580763.6028 | 627224.691 | 677402.6663 | 731594.8796 | 790122.47 | 853332.2676 | 921598.849 | 995326.7569 | 1074952.8975 | 1160949.1293 | 1253825.0596 | 1354131.0644 | 1462461.5495
14 | Heat pump instead of steam for hot water | 15 | -769780.6215 | 459701.9899 | 496478.1491 | 536196.4011 | 579092.1132 | 625419.4822 | 675453.0408 | 729489.2841 | 787848.4268 | 850876.3009 | 918946.405 | 992462.1174 | 1071859.0868 | 1157607.8137 | 1250216.4388 | 1350233.7539 | 0 | 0 | 0 | 0 | 0
15 | Return more condensate | 15 | -250000 | 100189.3242 | 108204.4701 | 116860.8277 | 126209.6939 | 136306.4694 | 147210.987 | 158987.8659 | 171706.8952 | 185443.4468 | 200278.9226 | 216301.2364 | 233605.3353 | 252293.7621 | 272477.2631 | 294275.4442 | 0 | 0 | 0 | 0 | 0
16 | Flue-gas economiser | 20 | -176634.9126 | 146639.8227 | 158371.0085 | 171040.6892 | 184723.9444 | 199501.8599 | 215462.0087 | 232698.9694 | 251314.8869 | 271420.0779 | 293133.6841 | 316584.3789 | 341911.1292 | 369264.0195 | 398805.1411 | 430709.5524 | 465166.3165 | 502379.6219 | 542569.9916 | 585975.5909 | 632853.6382
17 | Tune the burners on ovens, fryers and dryers: Tunnel oven burners (2 ovens) | 5 | -13000 | 282781.718 | 305404.2554 | 329836.5958 | 356223.5235 | 384721.4054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | Insulate the crate washer's soak tank and fit a lid | 15 | -10950 | 54450.6744 | 58806.7283 | 63511.2666 | 68592.1679 | 74079.5414 | 80005.9047 | 86406.3771 | 93318.8872 | 100784.3982 | 108847.1501 | 117554.9221 | 126959.3158 | 137116.0611 | 148085.346 | 159932.1737 | 0 | 0 | 0 | 0 | 0
19 | Recover oven flue heat: Tunnel oven burners (2 ovens) | 15 | -248410.8693 | 117967.9882 | 127405.4273 | 137597.8615 | 148605.6904 | 160494.1456 | 173333.6772 | 187200.3714 | 202176.4011 | 218350.5132 | 235818.5543 | 254684.0386 | 275058.7617 | 297063.4627 | 320828.5397 | 346494.8228 | 0 | 0 | 0 | 0 | 0
20 | Widen HVAC set points | 5 | -5600 | 6292.0764 | 6795.4425 | 7339.078 | 7926.2042 | 8560.3005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | Occupancy sensors in intermittently used areas | 10 | -14000 | 51662.7337 | 55795.7524 | 60259.4126 | 65080.1656 | 70286.5788 | 75909.5051 | 81982.2656 | 88540.8468 | 95624.1145 | 103274.0437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | LED lighting retrofit | 10 | -511600 | 251781.7143 | 271924.2514 | 293678.1915 | 317172.4469 | 342546.2426 | 369949.942 | 399545.9374 | 431509.6124 | 466030.3814 | 503312.8119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | Run on fewer transformers at light load | 10 | -15000 | 8083.037 | 8729.68 | 9428.0543 | 10182.2987 | 10996.8826 | 11876.6332 | 12826.7639 | 13852.905 | 14961.1374 | 16158.0283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | Power-factor correction | 15 | -136000 | 33611.1942 | 36300.0897 | 39204.0969 | 42340.4247 | 45727.6586 | 49385.8713 | 53336.741 | 57603.6803 | 62211.9747 | 67188.9327 | 72564.0473 | 78369.1711 | 84638.7048 | 91409.8012 | 98722.5853 | 0 | 0 | 0 | 0 | 0
| Portfolio net cash flow (R) |  | -3497273.8328 | 3266550.9928 | 3527875.0722 | 3810105.078 | 3974094.8118 | 4292022.3968 | 3435498.9207 | 3710338.8344 | 4007165.9412 | 4327739.2164 | 4673958.3538 | 3295859.0094 | 3559527.7301 | 3844289.9485 | 4151833.1444 | 4483979.796 | 1540119.214 | 1663328.7511 | 1796395.0512 | 1940106.6553 | 2095315.1877
| Discounted net cash flow (R) |  | -3497273.8328 | 2916563.3864 | 2812400.4083 | 2711957.5366 | 2525609.0982 | 2435408.7733 | 1740530.67 | 1678368.8604 | 1618427.1154 | 1560626.147 | 1504889.4988 | 947480.7077 | 913642.111 | 881012.0356 | 849547.32 | 819206.3443 | 251226.8056 | 242254.4197 | 233602.4761 | 225259.5306 | 217214.5473
| Cumulative net cash flow (R) |  | -3497273.8328 | -230722.84 | 3297152.2322 | 7107257.3101 | 11081352.122 | 15373374.5187 | 18808873.4395 | 22519212.2739 | 26526378.215 | 30854117.4315 | 35528075.7852 | 38823934.7946 | 42383462.5247 | 46227752.4733 | 50379585.6177 | 54863565.4136 | 56403684.6276 | 58067013.3788 | 59863408.43 | 61803515.0853 | 63898830.2731
| Discounted cumulative (R) |  | -3497273.8328 | -580710.4464 | 2231689.9619 | 4943647.4985 | 7469256.5967 | 9904665.37 | 11645196.04 | 13323564.9004 | 14941992.0158 | 16502618.1627 | 18007507.6616 | 18954988.3692 | 19868630.4802 | 20749642.5158 | 21599189.8358 | 22418396.1801 | 22669622.9857 | 22911877.4054 | 23145479.8816 | 23370739.4122 | 23587953.9595
Savings start in year 1 whatever the time to implement; a measure's savings stop at the end of its life and nothing is replaced (lib/ecosystem conventions).

## Portfolio
Portfolio
Per measure and in total: simple payback, NPV, IRR and the levelised cost of saved energy, then the cost curve (MACC). Same conventions as the studio's step 8.
FICTIONAL DEMONSTRATION: Demo Foods (Pty) Ltd (fictional). Every name and number is invented.
Key results
| Measures in the portfolio | 24
| Capex (R) | 3497273.8328
| Gross saving, year 1 (R/yr) | 3302505.4679
| Running cost change, year 1 (R/yr) | 35954.4752
| Net saving, year 1 (R/yr) | 3266550.9928
| Energy saved (kWh/yr) | 1873002.885
| Demand reduction (kVA) | 69.4667
| Simple payback (years) | 1.0706 | Total capex ÷ total year-1 net saving
| NPV (R) | 23587953.9595 | At the discount rate, over the analysis period (Inputs)
| IRR | 99.77% | Of the portfolio net cash flow
| Cost of saved energy (R/kWh) | 0.30506 | kWh-weighted LCSE of the measures on the cost curve
| Avoided energy rate on the curve (R/kWh) | 1.7445 | Energy charges saved ÷ kWh saved, curve measures
| Analysis period (years) | 20 | Longest measure life
| Weakest tag across the measures | assumed | 0 measured, 0 calculated, 0 estimated, 24 assumed
Measure by measure
# | Measure | System | Life n (whole years) | Capex (R) | Gross saving, year 1 (R/yr) | Running cost change (R/yr) | Net saving, year 1 (R/yr) | Energy saved (kWh/yr) | Simple payback (years) | NPV (R) | IRR | One IRR? | CRF (r, n) | LCSE (R/kWh) | Avoided energy rate (R/kWh) | On the cost curve (1/0) | Curve key (R/kWh) | Curve rank | LCSE × kWh (R/yr) | Tag
1 | Switch compressors off outside production | Compressed air | 5 | 15000 | 109789.3214 | 0 | 109789.3214 | 73358.3372 | 0.13663 | 441349.715 | 739.9% | Yes | 0.27741 | 0.056724 | 1.4966 | 1 | 0.056724 | 4 | 4161.146 | assumed
2 | Compressed-air leak repair programme | Compressed air | 5 | 45000 | 194759.2556 | 24000 | 170759.2556 | 130133.0127 | 0.26353 | 664777.0225 | 387.3% | Yes | 0.27741 | 0.28035 | 1.4966 | 1 | 0.28035 | 12 | 36483.4379 | assumed
3 | Duct the compressor intakes to outside air | Compressed air | 15 | 36000 | 21987.7229 | 0 | 21987.7229 | 14691.6182 | 1.6373 | 195122.0601 | 69% | Yes | 0.14682 | 0.35977 | 1.4966 | 1 | 0.35977 | 16 | 5285.6726 | assumed
4 | Variable-speed trim compressor | Compressed air | 15 | 518500 | 17328.9843 | 0 | 17328.9843 | 11578.7716 | 29.921 | -336347.8706 | -1.018% | Yes | 0.14682 | 6.5748 | 1.4966 | 1 | 6.5748 | 23 | 76128.3683 | assumed
5 | Variable-speed drive on a throttled pump (pump and system curves): Cooling-water and process pumps | Motors, pumps and fans | 10 | 82500 | 74560.8337 | 825 | 73735.8337 | 49819.5882 | 1.1189 | 479521.771 | 97.16% | Yes | 0.17698 | 0.30964 | 1.4966 | 1 | 0.30964 | 14 | 15426.1935 | assumed
6 | VSDs on the oven-hall extraction fans (2 × 22 kW) | Motors, pumps and fans | 10 | 98000 | 131618.6249 | 1000 | 130618.6249 | 87944.1038 | 0.75028 | 897587.9955 | 141.2% | Yes | 0.17698 | 0.20859 | 1.4966 | 1 | 0.20859 | 8 | 18344.4481 | assumed
7 | Synchronous or cogged belts instead of V-belts: Oven-hall extraction fans | Motors, pumps and fans | 10 | 19800 | 8552.4889 | 0 | 8552.4889 | 5714.5481 | 2.3151 | 45387.9106 | 49.53% | Yes | 0.17698 | 0.61322 | 1.4966 | 1 | 0.61322 | 22 | 3504.2865 | assumed
8 | Floating head pressure on the refrigeration plant | Refrigeration and chillers | 10 | 130000 | 136259.4487 | 0 | 136259.4487 | 91044.9802 | 0.95406 | 908582.9092 | 112.7% | Yes | 0.17698 | 0.25271 | 1.4966 | 1 | 0.25271 | 10 | 23007.9413 | assumed
9 | Refrigeration heat recovery: a desuperheater for hot water | Refrigeration and chillers | 15 | 200297.4294 | 235872.7458 | 0 | 235872.7458 | 126494.1142 | 0.84918 | 2279058.6688 | 125.8% | Yes | 0.14682 | 0.23249 | 1.8647 | 1 | 0.23249 | 9 | 29408.5178 | assumed
10 | Boiler combustion tuning and O2 trim | Steam and boilers | 10 | 85000 | 158828.527 | 8000 | 150828.527 | 85176.7497 | 0.56355 | 1064629.8556 | 185.4% | Yes | 0.17698 | 0.27054 | 1.8647 | 1 | 0.27054 | 11 | 23043.654 | assumed
11 | Steam trap survey and repair | Steam and boilers | 5 | 42000 | 261999.3803 | 15000 | 246999.3803 | 140505.3366 | 0.17004 | 984676.3235 | 596% | Yes | 0.27741 | 0.18968 | 1.8647 | 1 | 0.18968 | 7 | 26651.2087 | assumed
12 | Repair steam leaks | Steam and boilers | 3 | 7000 | 111786.4023 | 0 | 111786.4023 | 59948.9436 | 0.062619 | 281861.3187 | 1605% | Yes | 0.41635 | 0.048615 | 1.8647 | 1 | 0.048615 | 1 | 2914.4429 | assumed
13 | Insulate bare steam pipe, valves and flanges | Steam and boilers | 20 | 67200 | 338869.9842 | 0 | 338869.9842 | 181729.5947 | 0.19831 | 4311115.8407 | 512.3% | Yes | 0.13388 | 0.049506 | 1.8647 | 1 | 0.049506 | 2 | 8996.654 | assumed
14 | Heat pump instead of steam for hot water | Steam and boilers | 15 | 769780.6215 | 459701.9899 | 0 | 459701.9899 | 233672.3044 | 1.6745 | 4062337.343 | 67.64% | Yes | 0.14682 | 0.48368 | 1.9673 | 1 | 0.48368 | 18 | 113022.4544 | assumed
15 | Return more condensate | Steam and boilers | 15 | 250000 | 77918.7993 | -22270.5248 | 100189.3242 | 41786.3856 | 2.4953 | 803131.4715 | 47.71% | Yes | 0.14682 | 0.34546 | 1.8647 | 1 | 0.34546 | 15 | 14435.5351 | assumed
16 | Flue-gas economiser | Steam and boilers | 20 | 176634.9126 | 146639.8227 | 0 | 146639.8227 | 78640.177 | 1.2045 | 1718001.6404 | 91.02% | Yes | 0.13388 | 0.30071 | 1.8647 | 1 | 0.30071 | 13 | 23647.6666 | assumed
17 | Tune the burners on ovens, fryers and dryers: Tunnel oven burners (2 ovens) | Process heat | 5 | 13000 | 290781.718 | 8000 | 282781.718 | 155940.7626 | 0.045972 | 1162408.9998 | 2183% | Yes | 0.27741 | 0.074428 | 1.8647 | 1 | 0.074428 | 6 | 11606.3265 | assumed
18 | Insulate the crate washer's soak tank and fit a lid | Process heat | 15 | 10950 | 54450.6744 | 0 | 54450.6744 | 29200.8719 | 0.2011 | 561403.5849 | 505.3% | Yes | 0.14682 | 0.055057 | 1.8647 | 1 | 0.055057 | 3 | 1607.7254 | assumed
19 | Recover oven flue heat: Tunnel oven burners (2 ovens) | Process heat | 15 | 248410.8693 | 117967.9882 | 0 | 117967.9882 | 63264.0118 | 2.1057 | 991599.5017 | 55.28% | Yes | 0.14682 | 0.57652 | 1.8647 | 1 | 0.57652 | 21 | 36472.737 | assumed
20 | Widen HVAC set points | HVAC and offices | 5 | 5600 | 6292.0764 | 0 | 6292.0764 | 4204.2 | 0.89001 | 20553.6118 | 116.9% | Yes | 0.27741 | 0.36951 | 1.4966 | 1 | 0.36951 | 17 | 1553.4945 | assumed
21 | Occupancy sensors in intermittently used areas | Lighting | 10 | 14000 | 51662.7337 | 0 | 51662.7337 | 34519.68 | 0.27099 | 379778.4335 | 377% | Yes | 0.17698 | 0.071779 | 1.4966 | 1 | 0.071779 | 5 | 2477.7783 | assumed
22 | LED lighting retrofit | Lighting | 10 | 511600 | 251781.7143 | 0 | 251781.7143 | 168233.92 | 2.0319 | 1407504.9706 | 55.97% | Yes | 0.17698 | 0.53821 | 1.4966 | 1 | 0.53821 | 20 | 90545.0984 | assumed
23 | Run on fewer transformers at light load | Electrical supply and tariff | 10 | 15000 | 8083.037 | 0 | 8083.037 | 5400.8727 | 1.8557 | 46609.7023 | 60.89% | Yes | 0.17698 | 0.49154 | 1.4966 | 1 | 0.49154 | 19 | 2654.7625 | assumed
24 | Power-factor correction | Electricity supply: kVA demand and capacity | 15 | 136000 | 35011.1942 | 1400 | 33611.1942 | 0 | 4.0463 | 217301.1795 | 31.41% | Yes | 0.14682 | n/a | n/a | 0 | 0 |  | 0 | assumed
| Portfolio | 24 measures | 20 | 3497273.8328 | 3302505.4679 | 35954.4752 | 3266550.9928 | 1873002.885 | 1.0706 | 23587953.9595 | 99.77% | Yes |  | 0.30506 | 1.7445 | 23 |  |  | 571379.5503 | assumed
Cost curve of saved energy (MACC): cheapest saved kWh first, bar width = kWh saved a year
Rank | Measure | System | LCSE (R/kWh) | Energy saved (kWh/yr) | Cumulative from (kWh/yr) | Cumulative to (kWh/yr) | Against the avoided energy rate
1 | Repair steam leaks | Steam and boilers | 0.048615 | 59948.9436 | 0 | 59948.9436 | Costs less than the energy it saves
2 | Insulate bare steam pipe, valves and flanges | Steam and boilers | 0.049506 | 181729.5947 | 59948.9436 | 241678.5383 | Costs less than the energy it saves
3 | Insulate the crate washer's soak tank and fit a lid | Process heat | 0.055057 | 29200.8719 | 241678.5383 | 270879.4102 | Costs less than the energy it saves
4 | Switch compressors off outside production | Compressed air | 0.056724 | 73358.3372 | 270879.4102 | 344237.7474 | Costs less than the energy it saves
5 | Occupancy sensors in intermittently used areas | Lighting | 0.071779 | 34519.68 | 344237.7474 | 378757.4274 | Costs less than the energy it saves
6 | Tune the burners on ovens, fryers and dryers: Tunnel oven burners (2 ovens) | Process heat | 0.074428 | 155940.7626 | 378757.4274 | 534698.19 | Costs less than the energy it saves
7 | Steam trap survey and repair | Steam and boilers | 0.18968 | 140505.3366 | 534698.19 | 675203.5266 | Costs less than the energy it saves
8 | VSDs on the oven-hall extraction fans (2 × 22 kW) | Motors, pumps and fans | 0.20859 | 87944.1038 | 675203.5266 | 763147.6303 | Costs less than the energy it saves
9 | Refrigeration heat recovery: a desuperheater for hot water | Refrigeration and chillers | 0.23249 | 126494.1142 | 763147.6303 | 889641.7446 | Costs less than the energy it saves
10 | Floating head pressure on the refrigeration plant | Refrigeration and chillers | 0.25271 | 91044.9802 | 889641.7446 | 980686.7248 | Costs less than the energy it saves
11 | Boiler combustion tuning and O2 trim | Steam and boilers | 0.27054 | 85176.7497 | 980686.7248 | 1065863.4745 | Costs less than the energy it saves
12 | Compressed-air leak repair programme | Compressed air | 0.28035 | 130133.0127 | 1065863.4745 | 1195996.4872 | Costs less than the energy it saves
13 | Flue-gas economiser | Steam and boilers | 0.30071 | 78640.177 | 1195996.4872 | 1274636.6642 | Costs less than the energy it saves
14 | Variable-speed drive on a throttled pump (pump and system curves): Cooling-water and process pumps | Motors, pumps and fans | 0.30964 | 49819.5882 | 1274636.6642 | 1324456.2525 | Costs less than the energy it saves
15 | Return more condensate | Steam and boilers | 0.34546 | 41786.3856 | 1324456.2525 | 1366242.638 | Costs less than the energy it saves
16 | Duct the compressor intakes to outside air | Compressed air | 0.35977 | 14691.6182 | 1366242.638 | 1380934.2563 | Costs less than the energy it saves
17 | Widen HVAC set points | HVAC and offices | 0.36951 | 4204.2 | 1380934.2563 | 1385138.4563 | Costs less than the energy it saves
18 | Heat pump instead of steam for hot water | Steam and boilers | 0.48368 | 233672.3044 | 1385138.4563 | 1618810.7607 | Costs less than the energy it saves
19 | Run on fewer transformers at light load | Electrical supply and tariff | 0.49154 | 5400.8727 | 1618810.7607 | 1624211.6334 | Costs less than the energy it saves
20 | LED lighting retrofit | Lighting | 0.53821 | 168233.92 | 1624211.6334 | 1792445.5534 | Costs less than the energy it saves
21 | Recover oven flue heat: Tunnel oven burners (2 ovens) | Process heat | 0.57652 | 63264.0118 | 1792445.5534 | 1855709.5652 | Costs less than the energy it saves
22 | Synchronous or cogged belts instead of V-belts: Oven-hall extraction fans | Motors, pumps and fans | 0.61322 | 5714.5481 | 1855709.5652 | 1861424.1134 | Costs less than the energy it saves
23 | Variable-speed trim compressor | Compressed air | 6.5748 | 11578.7716 | 1861424.1134 | 1873002.885 | Costs more than the energy it saves
24
Off the curve: Power-factor correction (saves no kWh (its value is in demand, capacity or time-of-use charges)).

## Loan
Loan
If a term loan pays for the measures: the loan the savings can carry at a target DSCR, an annuity repayment, the DSCR by year and the equity cash flow (lib/ecosystem/loan.ts). A sizing sketch, not a term sheet.
FICTIONAL DEMONSTRATION: Demo Foods (Pty) Ltd (fictional). Every name and number is invented.
Loan settings (studio step 9; change them here or in the studio)
| Debt share of capex | 70% | assumed | LoanShare | 0 to 100%. Default 70%.
| Interest rate (nominal, all-in) | 11.5% | assumed | LoanRate | Default 11.5%: an assumed prime-linked rate. Use the bank's quote.
| Tenor (years) | 5 | assumed | LoanTenor | Whole years, 1 to 30; annual payments in arrears.
| Target minimum DSCR | 1.3 | assumed | TargetDSCR | The lender's minimum cover; confirm it with the bank.
Sizing and the lender's figures
| Capex (R) | 3497273.8328 | Year 0 of the portfolio net cash flow (CashFlows)
| Loan at the debt share (R) | 2448091.6829 | share × capex
| Capital recovery factor CRF(i, n) | 0.27398 | Level payment per rand borrowed
| Weakest net saving within the tenor (R) | 3266550.9928 | The weakest year binds a level payment
| Largest loan at the target DSCR (R) | 9171163.1573 | A_max ÷ CRF, A_max = weakest CFADS ÷ target DSCR
| Loan (R) | 2448091.6829 | The smaller of the two
| What sets the loan | Debt share
| Debt service a year (R) | 670732.4972 | Interest + principal, level
| Minimum DSCR | 4.8701 | Lenders size and set covenants on the weakest year
| Average DSCR | 5.6269 | Over the tenor
| Equity in (R) | 1049182.1498 | Capex less the loan
| Equity IRR | 257% | Of the equity cash flow
| Equity NPV (R) | 23618205.0982 | At the discount rate (Inputs)
| Meets the target in every year | Yes
Net saving = the portfolio's year-t cash flow (every measure in the studio's step 9). The report's lender view uses the firm measures only.
Debt schedule by year (nominal rand)
Year | Net saving, CFADS (R) | In the tenor (1/0) | CFADS within the tenor (R) | Opening balance (R) | Interest (R) | Debt service (R) | Principal (R) | Closing balance (R) | DSCR | Equity cash flow (R)
0 | -3497273.8328 | [6 empty] | 2448091.6829 |  | -1049182.1498
1 | 3266550.9928 | 1 | 3266550.9928 | 2448091.6829 | 281530.5435 | 670732.4972 | 389201.9537 | 2058889.7292 | 4.8701 | 2595818.4955
2 | 3527875.0722 | 1 | 3527875.0722 | 2058889.7292 | 236772.3189 | 670732.4972 | 433960.1784 | 1624929.5509 | 5.2597 | 2857142.5749
3 | 3810105.078 | 1 | 3810105.078 | 1624929.5509 | 186866.8983 | 670732.4972 | 483865.5989 | 1141063.952 | 5.6805 | 3139372.5807
4 | 3974094.8118 | 1 | 3974094.8118 | 1141063.952 | 131222.3545 | 670732.4972 | 539510.1428 | 601553.8092 | 5.925 | 3303362.3146
5 | 4292022.3968 | 1 | 4292022.3968 | 601553.8092 | 69178.6881 | 670732.4972 | 601553.8092 | 0 | 6.399 | 3621289.8995
6 | 3435498.9207 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 3435498.9207
7 | 3710338.8344 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 3710338.8344
8 | 4007165.9412 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 4007165.9412
9 | 4327739.2164 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 4327739.2164
10 | 4673958.3538 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 4673958.3538
11 | 3295859.0094 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 3295859.0094
12 | 3559527.7301 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 3559527.7301
13 | 3844289.9485 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 3844289.9485
14 | 4151833.1444 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 4151833.1444
15 | 4483979.796 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 4483979.796
16 | 1540119.214 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1540119.214
17 | 1663328.7511 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1663328.7511
18 | 1796395.0512 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1796395.0512
19 | 1940106.6553 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1940106.6553
20 | 2095315.1877 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 2095315.1877
21 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
22 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
23 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
24 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
25 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
26 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
27 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
28 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
29 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
30 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0

## Sources & methods
Sources & methods
How every figure in this workbook is worked out: the method notes of the audit engine, the sources they cite and the workbook's conventions.
FICTIONAL DEMONSTRATION: Demo Foods (Pty) Ltd (fictional). Every name and number is invented.
Method notes: each section's formulas and the method in plain words
Section | Formulas | Method | Applied on
1. Units and conversions | kWh = billed quantity × kWh per billing unit Diesel: 43.0 MJ/kg × 0.84 kg/l ÷ 3.6 = 10.03 kWh/l (net) LPG: 47.3 MJ/kg ÷ 3.6 = 13.14 kWh/kg (net); gross ≈ 1.086 × net Natural gas: 1 GJ = 277.78 kWh (gross, as billed); coal: 25.8 MJ/kg (net) Water below 100 °C: h ≈ 4.19 × T kJ/kg | One internal unit per quantity: kWh, kW, kVA, kg, °C, bar(g) and rand. Bills and nameplates are converted once, at the edge, and the factor and its source stay on the carrier account. Fuel factors are IPCC 2006 net calorific values (use the supplier's analysis where it exists). Saturated steam properties come from IAPWS-IF97 table values, interpolated in pressure. | Bills
2. Data levels | Level 1 (bills): E = share × metered total of the carrier Level 2 (inventory): E = n × P × LF × h / η Level 3 (interval): E = measured energy × annualisation factor Level 4 (process): energy and mass balance per process unit | The data level is set for each system (and can be overridden for a node), never for the whole site. Typical uncertainty: ±30% or worse at level 1, about ±20% at level 2, ±10-15% at level 3, ±5-10% at level 4. The levels follow the logic of ASHRAE Standard 211 audit levels and ISO 50002-1's proportionate data collection. A level-1 share is part of the bill it comes from, so it cannot confirm the balance; only level 2 and above test it. | Cover
3. Uncertainty | Product or quotient: u_rel = √(Σ u_rel,i²) Sum: u_abs = √(Σ u_abs,i²); u_rel = u_abs ÷ ¦Σ x_i¦ Difference a − b (a gap): u_abs = √(u_abs,a² + u_abs,b²) Defaults when none is stated: measured ±3%, calculated ±10%, estimated ±15%, assumed ±30% | Every number carries a tag and, where known, a ± (one standard uncertainty). Independent uncertainties combine in quadrature, the first-order method of the GUM (JCGM 100:2008). Through a model (the compressor plant, the steam system) each input is raised by its uncertainty in turn and the changes are added in quadrature. A result's tag is its weakest input's, never better than calculated. Inputs are treated as independent, so totals are slightly optimistic where one assumption is used on many items. | Inventory
4. Bottom-up energy of an item | E = n × P_rated × Σ_modes(LF × h) ÷ η (η = 1 for an input rating) u(E)² = u(n)² + u(P)² + u(Σ LF·h)² + u(η)² | n is the count, P the nameplate (the input, or the shaft output for motors), and the sum runs over the item's operating modes (for example baking and idle at temperature). The mode terms add as a sum for the uncertainty. The Inventory sheet holds this formula live for every item. | Inventory
5. The energy balance | Metered = Σ latest 12 bills × kWh per unit (× 12 ÷ n with fewer than 12 bills) Conversion: input = output ÷ η; loss = input − output gap = (E_metered − Σ E_i) ÷ E_metered Closes when ¦gap¦ ≤ 10% (5% where every node behind the point is at level 4) Optional scaling: k = (E_metered − Σ measured and calculated) ÷ Σ estimated and assumed | Sources, conversions (boiler, generator), boards, end uses, losses and an explicit unaccounted node are joined by flows of one carrier each. An end use takes measured data at level 3 or above, otherwise its system model's terms or E for each item, otherwise a level-1 share. A balance point is where a metered supply meets the estimated demand. The balance is never forced: the remainder is shown as unaccounted. Outside tolerance the contributors are ranked by kWh × ± for review. Scaling is optional, touches only estimated and assumed items, and is recorded. Mass streams are checked against the same tolerance. Benchmarks: LEED existing-buildings audits (end uses within 10% of the bills); the Australian EEO framework (80% of energy within ±5%). | Balance
6. System models and measures | state (from the inventory and survey) → annual energy by carrier measure: state before → state after; saving = energy before − energy after | Each modelled system has a plain state built from the register and its survey. A measure is a step that turns one state into the next, so the balance and the savings describe the same plant and the measures on one system can be applied in order (section 7). | Measures
6.1 Compressed air | Part load at capacity fraction C: load-unload u + (1 − u)C (u ≈ 0.25-0.35); modulation m₀ + (1 − m₀)C (m₀ ≈ 0.7); VSD (v₀ + (1 − v₀)C)(1 + δ) Pressure: specific power ∝ f(p) = (p_abs ÷ p_atm)^((k − 1) ÷ k) − 1, k = 1.4 Leak test: leak flow = capacity running × T_loaded ÷ (T_loaded + T_unloaded) Heat recovery: Q = E × recoverable share × used share; fuel displaced = Q ÷ heater efficiency Annual energy = Σ_blocks hours × plant kW at (end-use demand + leaks) | Identical units with ideal sequencing: all but one fully loaded, one trim unit at the remainder. Leaks scale with absolute pressure. The part-load shapes follow the US DOE / Compressed Air Challenge sourcebook; the coefficients are typical (assumed) until a CAGI data sheet or a kW log replaces them. Measures: switch off out of hours, lower the pressure, repair leaks to a target share, cooler intake air, a VSD trim compressor, heat recovery. | Measures
6.2 Steam | Failed trap (Napier, DOE Steam Tip Sheet #1): W (lb/h) = 24.24 × P (psia) × D² (in²) × severity Bare pipe: q' = π D (h_c + h_r)(T_s − T_a); h_c = 1.32 (ΔT ÷ D)^0.25 Feedwater F = S ÷ (1 − b); blowdown B = bF; make-up M = F − R Fuel = Q ÷ η; a better efficiency saves ΔF = F (1 − η₁ ÷ η₂) | A mass and energy balance of the steam system: steam raised for the users, trap and leak losses and pipe condensate; condensate returned; blowdown and make-up water, the feedwater temperature from mixing, and the boiler's fuel. Insulated pipe is solved for its surface temperature. It follows the system view of the DOE/NREL steam sourcebook. Measures: combustion tuning and O2 trim, automatic TDS control, trap survey and repair, leak repair, insulation, condensate return (the water and treatment saved is a negative running cost), blowdown heat recovery. | Measures
6.3 Refrigeration | COP = constant × T_e ÷ (T_c − T_e) (kelvin; a fixed fraction of Carnot) Same cooling load: E_new ÷ E_old = COP_old ÷ COP_new | About 1.5% per kelvin of lift for a freezer and 2.5-3% for a chiller, the conservative end of the 2-4% per °C screening figure. At level 3 the measured energy is shared over the node's items in proportion to their inventory estimates, so savings start from the measured figure. Measures: floating head pressure, condenser cleaning, a higher evaporating temperature, a new chiller at the end of its life, a desuperheater. | Measures
6.4 Lighting | E = n × W × h × f_on ÷ 1000 Occupancy sensors: f_on × (1 − r), r = 24% by default | LED retrofit at like-for-like watts from the supplier's data sheet, or a screening ratio by lamp type. The 24% is the average for occupancy sensing in the LBNL meta-analysis by Williams et al. (LEUKOS, 2012). Measures: switch-off campaign, occupancy and daylight controls, delamping, LED retrofit. | Measures
6.5 Motors, pumps and fans | E = P × LF × h ÷ η Higher-efficiency motor: ΔE = E (1 − η_old ÷ η_new) VSD: affinity laws over the flow duty (the site's motor and VSD tool) | VSDs go through the site's own motor and VSD tool, its baseline set to equal the inventory energy. IE minimum efficiencies come from IEC 60034-30-1:2014 (IE2 to IE4 also in Regulation (EU) 2019/1781, Annex I), interpolated in log kW. Full-load efficiencies only. | Measures
6.6 Electrical supply and tariff | Demand saving = kVA reduction × demand rate × 12 kVA reduction from the 12-bill means of kW and power factor at maximum demand | Power-factor correction, the NMD optimiser and solar PV go through the site's existing tools. Load shifting needs half-hourly data and the time-of-use rate table, so version 1 lists it as needing data. | Measures
6.7 Process heat and HVAC | Oven idle firing: E = n × P × LF_idle × h_idle (from the inventory's idle mode) | Idle firing is quantified from the register. Oven flue heat recovery is quantified from a flue-gas test on the oven (6.17). HVAC schedules and set points have their own module and model. | Measures
6.8 Heat pumps | Q = E_in × η_heater; E_hp = Q × c ÷ SCOP Saving: E_in × c on the heater's carrier; electricity added: E_hp From a calorifier: Q = m_steam × h_fg | The process keeps the heat it needs; a heat pump makes it instead of elements, a burner or a steam calorifier. A calorifier's steam comes off the steam model, so the boiler fuel and losses behind it go and the later steam measures see less steam. Defaults are assumed (SCOP 3.0 for about 60 °C water); the maker's data at the site's temperatures replaces them. The extra electrical demand is noted, not counted. | Measures
6.9 Boiler economiser | O₂,st = 2.664 C + 7.936 H + 0.998 S − O; air = O₂,st ÷ 0.2314 Excess air ≈ O₂ ÷ (20.9 − O₂) q = Σ m_i cp_i (T_in − T_out); r = q ÷ LHV Fuel saved = F × (1 − η ÷ (η + r)) | Flue-gas mass from the fuel's analysis and the excess air, cooled to a safe exit above the acid dew point (gas about 120 °C, oil 150 °C, coal 175 °C, plus 20 K). The boiler's efficiency rises by the share recovered, so less fuel is burned for the same heat. After O₂ trim it is worked out at the trimmed O₂ on the fuel that is left. | Measures
6.10 Compressor heat recovery | Recovered = min(E_comp × r × u, heat demand) Displaced = recovered ÷ η_heater, less the recovery circuit's pump | A share of the compressors' input (about 80-93% becomes heat, 50-90% of it recoverable, per the DOE / Compressed Air Challenge sourcebook) displaces boiler fuel or electric heating where a coincident heat demand takes it. Not netted against the steam measures, which cut the same fuel. | Measures
6.11 Chilled water and condensers | T_evap = T_chw − approach; T_cond = condenser fluid + approach Saving = E × (1 − COP_old ÷ COP_new), COP ∝ T_evap ÷ (T_cond − T_evap) | A warmer chilled-water supply and a cooler condenser cut the lift. The Carnot ratio gives about 3% per kelvin for a chiller (the physics, not the 2-4% rule of thumb, sets the number used). The condenser part is left to the floating-head measure on circuits still on fixed head pressure. | Measures
6.12 Pumps on their curves | System: h = h_s + (1 − h_s) q²; pump: h = h_0 − (h_0 − h_1) q² Throttled: P ∝ q h_pump(q) ÷ η(q) VSD: n = √((h_sys(q) + (h_0 − h_1) q²) ÷ h_0); P ∝ q h_sys(q) ÷ η(q ÷ n) ÷ η_drive | A more accurate companion to the public VSD tool for throttled and bypassed pumps: the static head, the pump curve and its efficiency curve (affinity laws), calibrated to the register's energy. With no static head it reduces to the cube law. Below the minimum speed the pump is held there and throttled. | Measures
6.13 Transformers | P = P₀ + P_k (S ÷ S_r)² E = P₀ h + P_k (S_peak ÷ S_r)² F_loss h; F_loss = 0.3 LF + 0.7 LF² Parallel units: Σ P₀ + (S ÷ Σ S_r)² Σ P_k | No-load and load losses from the nameplate or test certificate (Tier 1 maximum losses of EU Regulation 548/2014 when none is given). A lightly loaded unit of a parallel group can be switched off where the others carry the peak; at replacement, a right-sized low-loss unit. Savings count only when the site is metered on the medium-voltage side. | Measures
6.14 HVAC schedules and set points | Schedules: ΔE = E × r × (1 − a) Set points: 1 − DD_new ÷ DD_now, or p × ΔT (about 3% per °C cooling) | The HVAC model holds the air-conditioning and heating units (not IT or office equipment on the same node), so schedules and set points multiply. Hours cut and the pull-down allowance are assumed until a current log replaces them; the per-kelvin rules are tagged assumed and a site trial or degree-days replace them. | Measures
6.15 Belt drives | ΔE = E_motor × (1 − η_old ÷ η_new) V-belt about 93% in service, cogged 95%, synchronous 98% | A better belt passes more of the motor's output to the same load. Synchronous belts suit steady loads such as fans and pumps (check the speed: no slip means a little faster), cogged belts shock loads. Applied after a VSD on the same motor. | Measures
6.16 Boiler efficiency from a flue-gas test | Dry flue gas L_d = m_dry cp (T_flue − T_air) ÷ E; moisture L_m = m_water cp (T_flue − T_air) ÷ E (+ latent heat on the gross basis) η = 1 − L_d − L_m − L_casing (casing 1.5% of input when not entered, assumed) Direct: η = (S (h_g − h_fw) + B (h_f − h_fw)) ÷ fuel, B = S b ÷ (1 − b) Agree when ¦η_direct − η_losses¦ ≤ 2 √(u_direct² + u_losses²) | The losses method of BS 845-1, EN 12953-11 and ASME PTC 4 from a portable analyser's flue temperature and O₂ and the air temperature, with the flue products of the economiser module, on the same calorific-value basis as the fuel's bill. Where fuel and steam or feedwater were metered over one period the direct method checks it; a difference beyond their combined uncertainty points at a meter. The balance keeps the boiler's own efficiency until the auditor chooses the tested figure. | Balance
6.17 Oven flue heat recovery | Flue mass = fuel kWh × 3.6 ÷ LHV × flue products per kg of fuel (at the measured O₂) Recovered = m × cp × (T_flue − T_exit) × ε × u; displaced fuel = recovered ÷ η_heater Design kW = rated input × cp_fuel (T_flue − T_exit) ε ÷ LHV | From one flue-gas test on the oven's burner flue and its fuel a year (the register, or a gas meter). Defaults are assumed: exit at the fuel's safe minimum plus 20 K, 60% of the heat above it recovered, 80% of that used while the oven fires, the displaced heater 80% efficient. Priced per kW of design recovery from the cost library; not netted against idle-firing or hot-water measures that overlap it. Applies to direct- and indirect-fired ovens alike: the exhaust stream is real. | Measures
6.18 Compressor intake air | Same air, same pressure ratio: power ∝ T_intake (kelvin) Saving = plant energy × (1 − T_new ÷ T_now) | Ducting the intakes to outside air cuts the work of compressing the same mass of air by about 1% for every 3 K cooler. A step on the compressed-air model, after the switch-off, pressure and leak measures. Defaults are assumed: intake now 30 °C, outside 18 °C, both annual averages (a week of logging set against the weather station replaces them). Priced per compressor. | Measures
6.19 Hot surfaces and open tanks | Flat surface: q = (h_c + h_r)(T_s − T_a); h_c = 1.31 ΔT^(1/3) vertical, 1.52 ΔT^(1/3) facing up Insulated: k (T_hot − T_s) ÷ t = (h_c + h_r)(T_s − T_a) Open water: q_e = (p_w − p_a)(0.089 + 0.0782 V) kW/m², p in kPa Displaced = heat saved × hours ÷ heater efficiency | Simplified free convection to air (Holman) and radiation for bare tank walls; evaporation from open hot water by the pool equation (ASHRAE; fitted to pools, to confirm on a hot tank), with the Magnus saturation pressure. Insulation and an insulated lid are solved for their jacket temperature. The heat saved comes off the heater: steam at the boiler's efficiency, an element at 100% or a burner at 80% (assumed unless entered). Inputs on the opportunity: areas, temperatures, hours, emissivity. | Measures
6.20 Steam leaks | Napier, as for traps: W (lb/h) = 24.24 × P (psia) × D² (in²) Small 1.6 mm, medium 3.2 mm, large 6.4 mm hole | Leaks counted by size class on the walk-round join the steam model's baseline (lost, never returned) and the balance at the trap-loss node, ±40% because the size is judged by eye. The repair is a step on the steam model after the traps, 10% back by the next walk-round (assumed), priced per leak. | Measures
6.21 Blowdown | b = TDS_feedwater ÷ TDS_boiler; b_new = b × TDS_now ÷ TDS_set Recovered Q = B (h_f − c_p T_drain); make-up T_m + Q ÷ (M c_p); fuel saved = Q ÷ η | Automatic TDS control holds the boiler water just under its limit, so the blowdown falls in proportion (defaults 2,000 ppm now, 3,000 ppm set point, assumed); the make-up water saved is a negative running cost. A flash vessel and a plate exchanger return the blowdown's heat to the make-up water (drain 10 K above the make-up, assumed). Both are steps on the steam model; the recovery comes last and works on the blowdown that is left. | Measures
6.22 Stream-to-stream heat recovery | C = ṁ c_p; Q = ε × C_min × (T_hot,in − T_cold,in) Recovered a year = Q × coincident hours; displaced = recovered ÷ heater efficiency | The effectiveness method for a plate exchanger between a hot stream to drain or cooling and a stream being heated. Inputs on the opportunity: both flows and inlet temperatures; defaults (assumed) water on both sides, ε 0.7, the site's operating hours. Priced per kW of duty; the pumps' electricity is not deducted. | Measures
6.23 Desuperheater | Condenser heat Q_c = E (1 + COP), COP = 0.5 × Carnot COP Recovered = s × Q_c × u; displaced = recovered ÷ heater efficiency | The compressors' hot discharge gas carries a share of the condenser heat as superheat (about 10-15%; 10% assumed, to confirm against the discharge temperature) that can preheat water; half of it is taken as meeting a coincident demand (assumed). A step on the refrigeration model, after the lift measures; the compressors' energy is unchanged and the water heater's fuel is saved. | Measures
6.24 Burner tuning | η = 1 − dry flue-gas loss − moisture loss (losses method) at today's and the target O₂ Fuel saved = F (1 − η_now ÷ η_tuned) | From a flue-gas test on the burner's own flue (temperature and O₂), with the flue temperature held. Target O₂ (assumed, conservative for ovens; agree it with the burner's maker): LPG and natural gas 4%, diesel 5%, coal 7%, against US DOE's 10-20% excess air at high fire (about 2-3.5% O₂) and an Oregon State IAC report's 4% for natural-gas ovens. Only for indirect-fired ovens (the burner in its own firebox or radiant tubes, with its own flue): in a direct-fired oven the exhaust O₂ includes air drawn through the oven and would overstate the saving, so the measure does not apply (match the exhaust fan to the oven instead: about 5%, Carbon Trust CTS402); firing not recorded is quantified with a note to confirm it. Priced per burner with a yearly re-tune. Tuning leaves less flue gas, so a flue heat recovery on the same oven is worked out after it, on the fuel left and at the target O₂ (demo: 111.5 → 63.3 MWh), and the two do not overlap. | Measures
6.25 End-of-life replacement | E_new = E × COP_now ÷ COP_new (EER, or SEER, on the same basis) | A step on the HVAC model for air-conditioning units and on the refrigeration model for chilled-water circuits. Defaults (assumed): splits EER 2.6 now and 3.6 new, chillers COP 2.8 and 3.8, until the nameplate and the maker's figure at the same rating conditions replace them. Priced per kW of cooling; where the units are due for replacement anyway, only the extra cost of the efficient unit belongs here (a quote). | Measures
6.26 Daylight and delamping | Daylight: f_on × (1 − r), r = 28% by default Delamping: n_new = ⌈n × E_required × 1.25 ÷ E_measured⌉ | Daylight or photocell control saves 28% of the on-time on average (the LBNL meta-analysis) in daylit halls and stores and for outdoor lights on timers. Delamping takes fittings out of an area a lux survey finds over-lit, keeping a 25% margin over the level its task needs (from SANS 10114-1, to confirm). Both are steps on the lighting model, before the LED retrofit. | Measures
7. Sequencing interacting measures | Order: behaviour → controls → maintenance → retrofit → technology → heat recovery Overlap removed = Σ savings on their own − Σ sequenced savings | Measures on one system are applied in order, each on the state the earlier ones left (heat recovery last, because it recovers from what is left), as US DOE MEASUR does for compressed air. The direction of an interaction comes out of the model: fixing leaks first can leave a VSD trim compressor little to save. Systems without a model keep each measure's own saving with a warning; cross-system effects are noted, not netted. The Measures sheet holds the sequenced savings. | Measures
8. EnPIs and baselines | Intensity = kWh ÷ production (kWh/t) or ÷ floor area (kWh/m²) Baseline: E = b₀ + Σ b_j x_j by least squares, β = (XᵀX)⁻¹ Xᵀ y CV(RMSE) = 100 × √(Σ(y − ŷ)² ÷ (n − p)) ÷ ȳ; NMBE = 100 × Σ(y − ŷ) ÷ ((n − p) ȳ) Monthly data pass when CV(RMSE) ≤ 15% and ¦NMBE¦ ≤ 5% | Regression baselines against the relevant variables (production, degree-days) follow ISO 50006:2023; the fit statistics and thresholds are ASHRAE Guideline 14-2014's. R² ≥ 0.75 is shown only as a rule of thumb. Non-routine adjustments (a new line, a long shutdown) are recorded and added to the baseline's prediction, as IPMVP and SANS 50010 require. The baselines are in the report (not on a sheet here). | The report (EnPIs and baselines)
9. Rates and the business case | Energy rate = energy charges ÷ kWh; demand rate = demand charges ÷ billed kVA; capacity rate = capacity charges ÷ (NMD × months) LCSE = (capex × CRF + Δopex) ÷ kWh saved; CRF = r (1 + r)^n ÷ ((1 + r)^n − 1) NPV, IRR and payback as set out under Conventions below | Savings are priced at average rates from the latest 12 bills. An average energy rate suits a saving spread like the site's load; one in peak or off-peak hours is worth more or less. Energy savings claim no demand (kVA) saving unless the measure is a demand measure. The levelised cost of saved energy is the measure developed at LBNL (Meier; Hoffman et al., The Cost of Saving Electricity). | Portfolio
9.1 Financing view (loan) | CFADS_t = the portfolio's net saving in year t (0 past the longest life) A = D × CRF(i, n); interest_t = opening_t × i; principal_t = A − interest_t DSCR_t = CFADS_t ÷ A; minimum and average over the tenor A_max = max(0, min_t CFADS_t) ÷ DSCR_target; D_max = A_max ÷ CRF(i, n); D = min(share × capex, D_max) Equity_0 = −(capex − D); Equity_t = CF_t − A (t ≤ n), CF_t after | What a bank's credit committee reads if a term loan pays for the measures: the loan the savings can carry, a level (annuity) repayment and the debt service cover ratio each year. With level payments the weakest year binds, so the loan is the smaller of the debt share and what the target cover allows. Lenders look at the minimum DSCR because a loan defaults in its worst year; the average is a second look (Yescombe). Defaults are assumed: 70% of capex, 11.5% nominal (prime-linked), 5 years, 1.30×. No tax, fees, grace period or reserve account. | Loan
10. Screening ranges | None: ranges flag what is worth a look and are never used in a measure's numbers | Ranges, each with its source: compressed air savings up to a third (Carbon Trust); leakage 5-10% managed against 40-50% unmanaged (BCAS); steam systems 10-20% (DOE/NREL); motor systems 20-30% (IEA, 2011); IE-class upgrades a few percent of motor energy; occupancy sensing about 24% and daylighting about 28% (LBNL); refrigeration 2-4% per °C of lift (Carbon Trust). | —
11. Data requests and better data | Uncertainty removed = saving × (u_now − u_next) (typical ± of the current and the next data level) | The data request lists what to ask the client for, cumulative by level and limited to the systems the site type usually has. For each system, the studio shows what would raise it one level, which savings would firm up, and the opportunities still waiting for data, sorted by the rand a year of uncertainty removed. | —
12. The demo site | Monthly bills = base + kWh per tonne × production + kWh per degree-day × CDD + a fixed scatter | Demo Foods (Pty) Ltd is fictional: every number is invented and listed with its assumption, and the bills are generated from stated formulas so they agree with the production and weather series. It applies only to the demonstration workbook. | Cover
13. Version 1 simplifications | — | Independent uncertainties, no Monte Carlo. Compressors of different sizes are averaged into identical units; receivers and pressure bands are not modelled. Steam: trap steam is taken as lost; flash steam and deaerator venting are not modelled. Refrigeration: a constant fraction of Carnot, no part-load or defrost interaction. Motors: full-load efficiencies. One carrier per balance point; several suppliers of one carrier share a node's estimate equally. Cross-system interactions are warned about, not netted; process heat has no model: flue heat recovery is worked out after burner tuning on the same oven, but hot surfaces, stream-to-stream recovery and idle firing are not netted against each other. Hot surfaces: flat surfaces in still air, evaporation by a pool correlation. | —
14. Cost library | Rate = value × installation factor × (1 + e)^(base year − price year) Capex = Σ quantity × rate; u = (high − low) ÷ (2√3) per line, in quadrature | Every capex and running cost is a quantity times a unit cost from the cost library. The defaults are assumed placeholder 2026 budget figures, to be replaced by supplier quotes. Strongest first: a quote on the opportunity, a rate typed on it, this project's price for the record, a survey figure, the placeholder. The lines are kept in each measure's provenance. | Measures
15. Interval data (level 3) | P = E × 60 ÷ Δt (kWh per interval to average kW), × the multiplier E = Σ P Δt; load factor = P̄ ÷ P_max; annualised × 8 760 ÷ hours covered Baseload = P5 of nights and weekends; after hours above it = Σ max(0, P − P_base) Δt outside operating hours Peak shaving at T: Σ max(0, P − T) Δt; the worst day's energy and P_max − T | Half-hourly or logged data per meter, read as confirmed (kW or kWh checked against the bills, the multiplier, start or end stamps, SAST) and put on a regular grid. Gaps stay gaps; short ones are interpolated only by a recorded, flagged rule. Load profile, load duration, time-of-use split on a default Eskom-style schedule to verify against the tariff book, peaks, monthly reconciliation with the bills and a daily baseline. A good year moves the systems it covers to level 3. | —
16. Recirculation loops | Condensate return: L = R × c_p × (T_c − T_m) ÷ 3 600 (kWh a year; above make-up water) Boiler: in = fuel + L; out = steam + L + blowdown + flue loss Steam mains: in = steam + L; out = users + traps + pipe loss + L Feedwater already holds it: F × c_p × (T_fw − T_m) = R × c_p × (T_c − T_m) | A link marked as recirculation (condensate return, recovered heat) carries energy back upstream and is drawn as a loop. Its energy comes from the steam model or the auditor's own figure, counted above make-up water so nothing is negative. It adds the same energy in and out of every node on its path, so no balance figure changes: the balance and this workbook give the once-through figures, and the diagram adds the loop to the links it rides on. The blowdown's share of the condensate's heat (b × L) stays in the steam, where the steam model counts it. Demo: 52.0 MWh a year from the steam mains back to the boiler. | —
Sources the methods cite (pages and clauses to confirm against the reference library before a report quotes them)
Used for | Source | Public page | Status
audit process, data collection, energy balance | ISO 50002-1:2025, Energy audits, Part 1: general requirements | https://www.iso.org/search.html?q=50002-1 | confirm clauses
audit levels | ASHRAE Standard 211-2018, Commercial Building Energy Audits | https://www.ashrae.org/technical-resources/standards-and-guidelines | confirm section
regression baselines, relevant variables | ISO 50006:2023, EnPIs and energy baselines | https://www.iso.org/search.html?q=50006 | confirm clauses
CV(RMSE), NMBE and their thresholds | ASHRAE Guideline 14-2014, Measurement of Energy, Demand and Water Savings | https://www.ashrae.org/technical-resources/standards-and-guidelines | confirm section and table
M&V, non-routine adjustments | EVO, IPMVP Core Concepts; SANS 50010 | https://evo-world.org/ | confirm edition
10% end-use reconciliation benchmark | LEED existing buildings (O+M) energy audit requirement | https://www.usgbc.org/leed | as summarised in the design spec; confirm
80% within ±5% benchmark | Australian Energy Efficiency Opportunities, assessment framework | No public page: a printed or purchased source | as summarised in the design spec; confirm
uncertainty propagation | JCGM 100:2008 (GUM) | https://www.bipm.org/en/committees/jc/jcgm/publications | section 5.1
net calorific values | IPCC 2006 Guidelines, Vol. 2, ch. 1, Table 1.2 | https://www.ipcc-nggip.iges.or.jp/public/2006gl/ | confirm table values
propane gross/net ratio | NIST Chemistry WebBook | https://webbook.nist.gov/chemistry/ | —
saturated steam properties | IAPWS-IF97 (via standard steam tables) | https://www.iapws.org/ | —
part-load curves, leak test, heat recovery | US DOE / Compressed Air Challenge, Improving Compressed Air System Performance (sourcebook) | https://www.compressedairchallenge.org/ | confirm edition and pages
ordered evaluation of measures | US DOE MEASUR | No public page: a printed or purchased source | —
screening ranges | Carbon Trust compressed air and refrigeration guides | https://www.carbontrust.com/ | confirm edition and pages
leakage screening range | British Compressed Air Society (BCAS) | https://www.bcas.org.uk/ | confirm document
trap and leak losses, steam system | US DOE Steam Tip Sheet #1; DOE/NREL Improving Steam System Performance sourcebook | No public page: a printed or purchased source | confirm pages
simplified free-convection correlation | J. P. Holman, Heat Transfer | No public page: a printed or purchased source | confirm edition and table
IE minimum efficiencies | IEC 60034-30-1:2014; Regulation (EU) 2019/1781, Annex I | https://eur-lex.europa.eu/eli/reg/2019/1781/oj | check the table values before client use
motor-system screening range | IEA (2011), Energy-Efficiency Policy Opportunities for Electric Motor-Driven Systems | https://www.iea.org/ | confirm page
occupancy-sensor and daylighting savings | Williams et al. (2012), Lighting Controls in Commercial Buildings, LEUKOS 8(3) | No public page: a printed or purchased source | —
cost of saved energy | LBNL: Meier (1982); Hoffman et al., The Cost of Saving Electricity | https://emp.lbl.gov/ | —
heat pump COP test conditions (the maker's data) | EN 14511; EN 16147 | https://standards.cencenelec.eu/ | confirm editions
stoichiometric air and flue-gas products | Babcock & Wilcox, Steam: Its Generation and Use (combustion calculations) | https://www.babcock.com/ | confirm edition and chapter
O₂ to excess air, minimum flue exit, economiser screening range | US DOE Steam Tip Sheets #3 (feedwater economizers) and #4 (combustion efficiency) | https://www.energy.gov/ | confirm
ideal-gas cp of flue products | Çengel and Boles, Thermodynamics: An Engineering Approach, Table A-2(b); NIST Chemistry WebBook | https://webbook.nist.gov/chemistry/ | confirm values
boiler efficiency by losses and by input and output, casing loss | BS 845-1; EN 12953-11; ASME PTC 4, Fired Steam Generators | https://www.asme.org/codes-standards | confirm editions and clauses
independent check of the flue-gas losses (tests) | Siegert's flue-gas loss formula, as in Germany's 1. BImSchV, Annex III | No public page: a printed or purchased source | confirm coefficients
coverage factor 2 for the two efficiency methods' agreement | JCGM 100:2008 (GUM), 6.3 | https://www.bipm.org/en/committees/jc/jcgm/publications | —
recoverable heat 80-93% × 50-90% | US DOE / Compressed Air Challenge sourcebook, "Heat Recovery with Compressed Air Systems" | https://www.compressedairchallenge.org/ | confirm page
pump and system curves, affinity laws | Hydraulic Institute and Europump, Variable Speed Pumping (2004); US DOE Improving Pumping System Performance (2006) | https://www.pumps.org/ | confirm pages
transformer loss factor | T. Gönen, Electric Power Distribution Engineering (Buller and Woodrow loss factor) | No public page: a printed or purchased source | confirm edition and page
Tier 1 transformer losses | Commission Regulation (EU) No 548/2014, Annex I, Table I.1 | https://eur-lex.europa.eu/eli/reg/2014/548/oj | check the values before client use
about 3% per °C of cooling set point | Hong Kong EMSD indoor set-point guidance | No public page: a printed or purchased source | confirm document
up to about 8% per °C of heating set point | Carbon Trust heating guidance | https://www.carbontrust.com/ | confirm document
degree-day method | ASHRAE Handbook, Fundamentals, energy-estimating chapter | https://www.ashrae.org/technical-resources/ashrae-handbook | confirm edition
V-belt, cogged and synchronous belt efficiencies | US DOE Motor Systems Tip Sheet #5 | https://www.energy.gov/ | confirm edition
compressor power and intake temperature | G. F. C. Rogers and Y. R. Mayhew, Engineering Thermodynamics: Work and Heat Transfer (compression work) | No public page: a printed or purchased source | confirm edition and chapter
evaporation from open hot water | ASHRAE Handbook, HVAC Applications, natatorium chapter (Carrier's evaporation equation) | https://www.ashrae.org/technical-resources/ashrae-handbook | confirm edition and page; fitted to pools
saturation vapour pressure | Alduchov and Eskridge (1996), Improved Magnus form approximation of saturation vapor pressure, J. Applied Meteorology 35(4) | No public page: a printed or purchased source | —
blowdown from TDS, blowdown heat recovery | US DOE Steam Tip Sheets #9 (Minimize Boiler Blowdown) and #10 (Recover Heat from Boiler Blowdown) | https://www.energy.gov/ | confirm
boiler-water limits behind the TDS set point | EN 12953-10, Shell boilers: feedwater and boiler water quality | https://standards.cencenelec.eu/ | confirm edition and table
stream-to-stream heat recovery | Incropera and DeWitt, Fundamentals of Heat and Mass Transfer (effectiveness method) | No public page: a printed or purchased source | confirm edition and chapter
desuperheat share of the condenser heat, about 10-15% | ASHRAE Handbook, Refrigeration (heat reclaim) | https://www.ashrae.org/technical-resources/ashrae-handbook | confirm chapter, edition and figure
about 10-20% excess air (2-3.5% O₂) at high fire for furnaces and ovens; burner tuning target O₂ | US DOE Process Heating Tip Sheet #2, Check Burner Air to Fuel Ratios | https://www.osti.gov/biblio/920937 | confirm page
natural-gas ovens tuned yearly to about 4% O₂; burner tuning target O₂ | Oregon State University Industrial Assessment Center, assessment report OR0702 (oven tuning and recirculation) | No public page: a printed or purchased source | confirm page
direct-fired ovens: flue losses about 20% of gas use, exhaust fans matched to the oven gases about 4.7% (1-5 year payback) | Carbon Trust CTS402, Improving the efficiency of bakery ovens | https://www.carbontrust.com/ | confirm pages
EER and COP at rating conditions (end-of-life replacement) | ISO 5151; AHRI 550/590 | https://www.iso.org/search.html?q=5151 | confirm editions
light levels by area (delamping) | SANS 10114-1, Interior lighting | No public page: a printed or purchased source | confirm the table values
rectangular range to standard uncertainty (cost ranges) | JCGM 100:2008 (GUM), 4.3.7 | https://www.bipm.org/en/committees/jc/jcgm/publications | —
public holidays and the Sunday rule | Public Holidays Act 36 of 1994 (South Africa) | No public page: a printed or purchased source | —
the default TOU schedule, shipped labelled "verify against the current Eskom tariff book" | Eskom tariff book (Megaflex time-of-use periods) | No public page: a printed or purchased source | confirm the current periods and holiday rules
default limits for the daily baseline | ASHRAE Guideline 14-2014 (hourly calibration limits) | https://www.ashrae.org/ | confirm section and table
spike test (median and scaled MAD) | Hampel (1974), the influence curve; Pearson (2002) on the Hampel filter | No public page: a printed or purchased source | —
percentiles | Hyndman and Fan (1996), Sample quantiles in statistical packages (type 7) | No public page: a printed or purchased source | —
heat in returned condensate above make-up water | US DOE Steam Tip Sheet #8, Return Condensate to the Boiler | https://www.energy.gov/ | confirm
steady-flow energy balance and its reference state (the loops) | Çengel and Boles, Thermodynamics: An Engineering Approach, chapter 5 (mass and energy analysis of control volumes) | No public page: a printed or purchased source | confirm edition and pages
cover ratios (DSCR, minimum and average), debt sizing to a target cover, annuity repayment | E. R. Yescombe, Principles of Project Finance, 2nd edition (Academic Press, 2014) | No public page: a printed or purchased source | confirm chapter and pages
annuity debt sized by the weakest year's cover, as in the debt-sizing tool | Edward Bodmer, project finance debt sizing and sculpting (edbodmer.com) | https://edbodmer.com/sculpting-course/ | —
Public pages are the publishers' own; standards are sold by their publishers, so the page is where to buy or find the edition cited.
Conventions in this workbook (the same as the studio's business case)
Money is nominal rand. Cash flows are annual and at the end of each year; year 0 is now and is not discounted.
CF0 = −capex. CFt = S × (1 − d)^(t−1) × (1 + e)^(t−1) − O × (1 + e)^(t−1) for t = 1 to n, then 0: S is the year-1 rand saving, d its yearly decay, e the escalation, O the year-1 change in running costs.
n is the measure's life rounded to whole years (1 to 60). Savings start in year 1 whatever the time to implement, and stop at the end of the life; nothing is replaced.
NPV = CF0 + NPV(r, CF1:CFn). The spreadsheet's NPV discounts its first value by one year, so year 0 is added outside it.
IRR is the spreadsheet's IRR from its 10% starting guess; the studio takes the root nearest 10%. Where a cash flow has more than one IRR the Portfolio sheet says so: read the NPV.
Simple payback = capex ÷ year-1 net saving (n/a when the net saving is not positive).
Levelised cost of saved energy (LCSE) = (capex × CRF(r, n) + Δopex) ÷ kWh saved a year, with CRF = r(1 + r)^n ÷ ((1 + r)^n − 1), or 1/n at r = 0. The portfolio figure is the kWh-weighted LCSE of the measures on the cost curve.
The cost curve (MACC) sorts the measures that save kWh by LCSE, cheapest first; bar width is the kWh saved a year. Measures that save no kWh (demand or capacity charges only) sit outside it.
Measures on one system are sequenced by the studio, so their savings do not overlap; the workbook takes the sequenced figures.
Each number carries a tag: measured, calculated, estimated or assumed. A result is only as good as its weakest input.
Demo Foods (Pty) Ltd is fictional; nothing in this workbook comes from a real company, client or employer.